## Overview_data
GOLD_E_F_Modbus_260227
Modbus RTU/TCP
GOLD RX/PX/CX/SD, GENERATION E/F
Applicable to program version 1.09 and newer versions
Overview
ModBus can access single addresses or multiple addresses
simultaneously; either reading or writing single bit values
or 16-bit values.
A ModBus address contains either a 1-bit discrete value or
a 16-bit integer value.
ModBus data format
ModBus data types are 1-bit values and 16-bit values.
ModBus Type |  | Description | Reference
Coli Status |  | Discrete Output | 0x
Input Status |  | Discrete Input | 1x
Holding Register |  | 16-bit Output Register | 4x
Input Register |  | 16-bit Input Register | 3x
Supported ModBus commands
The GOLD air handling unit supports these ModBus commands.
Function code | Description
01 | Read Coil Status
02 | Read Input Status
03 | Read Holding Registers
04 | Read Input Registers
05 | Force Single Coil
06 | Present Single Registers
08 | Diagnostics.Sub-funktion 00 Only - Return Query Data (loop back).
15 | Force Multiple Colis
16 | Present Multiple Registers

## Overview parameters
GOLD_E_F_Modbus_260227
Operation level | 3x0592 | EA AHU filter pressure level |  | 3x0029 |  | EA Temperature |  | 3x0066
Communication operation level | 4x0793 | EA AHU filter pressure alarm limit. |  | 3x0030 |  | EA/Room temperature set point |  | 4x0135
Operation active | 1x0001 |  |  |  |  | SA min temp set point |  | 4x0136
Low speed operation active | 1x0003 |  |  |  |  | SA max temp set point |  | 4x0137
High speed operation active | 1x0004 |  | EA Duct pressure |  | 3x0010
Damper operation active | 1x0002 |  | EA low speed pressure set point |  | 4x0020
Triggered alarm #1 | 3x0604 |  | EA high speed pressure set point |  | 4x0022 | SA Duct pressure |  | 3x0008
A-alarm active | 1x0013 |  |  |  |  | SA low speed pressure set point |  | 4x0019
B-alarm active | 1x0014 |  |  |  |  | SA high speed pressure set point |  | 4x0021
Alarm reset | 0x0001
[6 empty] | SA Temperature |  | 3x0064
EA Air flow | 3x0006 |  |  |  |  | SA temperature set point |  | 4x0132
EA Fan level | 3x0038 |  |  |  |  | ERS 1 diff |  | 4x0118
EA low speed air flow set point | 4x0004
EA high speed air flow set point | 4x0006
Outdoor temperature | 3x0073
SA AHU filter pressure level | 3x0027
SA AHU filter pressure alarm limit. | 3x0028
RX
Heat exchanger regulator level | 3x0091
RHX operation level | 3x0105
PX | [6 empty] | Cool regulator level | 3x0101
PHX-2 Damper 2 output | 3x0123 | [5 empty] | Cool output 1 | 1x0043
PHX-2 Bypass output | 3x0125 | [5 empty] | Cool output 2 | 1x0044
PHX-2 Damper 1 output | 3x0121
CX |  | SA Air flow |  | 3x0004 | Reheat regulator level |  | 3x0094
CHX-2 Valve output | 3x0137 | SA Fan level |  | 3x0037 | Re-heat output |  | 1x0038
CHX-2 Pump output | 3x0139 | SA low speed air flow set point |  | 4x0003 | Re-heat anti frost temp/overheat input |  | 3x0153
CHX-1 pump output | 1x0027 | SA high speed air flow set point |  | 4x0005

## Coil Status
GOLD_E_F_Modbus_260227
Coil Status. 1bit (R/W).
Modbus | Name | Description | Min | Max | Unit | Default | Misc
Alarm settings
0x0001 | Alarm reset | Resets all active alarms | 0 | 1 |  | 0
0x0002
0x0003 | Internal fire alarm function
0x0004 | Internal fire alarm reset function | 0=manual reset, 1=auto reset | 0 | 1 |  | 0
0x0005
0x0006 |  |  | 0 | 1 |  | 0
0x0007 | External fire alarm no. 1 reset function | 0=manual reset, 1=auto reset | 0 | 1 |  | 0
0x0008 | External fire alarm no. 2 reset function | 0=manual reset, 1=auto reset
0x0009
0x0010
0x0011 | External alarm no. 1 reset function | 0=manual reset, 1=auto reset | 0 | 1 |  | 0
0x0012 | External alarm no. 2 reset function | 0=manual reset, 1=auto reset | 0 | 1 |  | 0
0x0013
0x0014
0x0015 | External alarm no. 1 input function | 0=alarm at closed contact, 1=alarm at open contact | 0 | 1 |  | 0
0x0016 | External alarm no. 2 input function | 0=alarm at closed contact, 1=alarm at open contact | 0 | 1 |  | 0
0x0017
0x0018
0x0019
0x0020
0x0021
0x0022
0x0023
0x0024
0x0025
0x0026
0x0027
0x0028
Pressure sensors zero point calibration
0x0029 | SA flow pressure sensor auto zero calibration |  | 0 | 1 |  | 1
0x0030 | EA flow pressure sensor auto zero calibration |  | 0 | 1 |  | 1
0x0031 | SA duct pressure sensor auto zero calibration |  | 0 | 1 |  | 1
0x0032 | EA duct pressure sensor auto zero calibration |  | 0 | 1 |  | 1
0x0033 | ReCO2 pressure sensor auto zero calibration |  | 0 | 1 |  | 1
0x0034 | RHX defrost pressure sensor auto calibration |  | 0 | 1 |  | 1
0x0035 | Carry over control pressure sensor auto calibration |  | 0 | 1 |  | 1
0x0036 | SA filter pressure sensor auto zero calibration |  | 0 | 1 |  | 1
0x0037 | EA filter pressure sensor auto zero calibration |  | 0 | 1 |  | 1
0x0038 | SA pre-filter pressure sensor auto zero calibration |  | 0 | 1 |  | 1
0x0039 | EA pre-filter pressure sensor auto zero calibration |  | 0 | 1 |  | 1
0x0040 | SA end-filter pressure sensor auto zero calibration |  | 0 | 1 |  | 1
0x0041 | PX heat exchange pressure sensor auto calibration |  | 0 | 1 |  | 1 | 1.21
0x0042 | Air quality control pressure sensor auto calibration |  | 0 | 1 |  | 1 | 2.42
0x0043 | HC defrost sensor auto calibration |  | 0 | 1 |  | 1 | 2.42
0x0044
0x0045
0x0046 | SA flow pressure sensor activate zero calibration | If value is set to 1 for min 1s calibration will be performed. | 0 | 1 |  | 0
0x0047 | EA flow pressure sensor activate zero calibration |  | 0 | 1 |  | 0
0x0048 | SA duct pressure sensor activate zero calibration |  | 0 | 1 |  | 0
0x0049 | EA duct pressure sensor activate zero calibration |  | 0 | 1 |  | 0
0x0050 | ReCO2 pressure sensor activate calibration |  | 0 | 1 |  | 0
0x0051 | RHX Defrost pressure sensor activate calibration |  | 0 | 1 |  | 0
0x0052 | Carry over control pressure sensor activate zero calibration |  | 0 | 1 |  | 0
0x0053 | SA filter pressure sensor activate zero calibration |  | 0 | 1 |  | 0
0x0054 | EA filter pressure sensor activate zero calibration |  | 0 | 1 |  | 0
0x0055 | SA pre-filter pressure sensor activate zero calibration |  | 0 | 1 |  | 0
0x0056 | EA pre-filter pressure sensor activate zero calibration |  | 0 | 1 |  | 0
0x0057 | SA end-filter pressure sensor activate zero calibration |  | 0 | 1 |  | 0
0x0058 | PX heat exchange pressure sensor activate zero calibration |  | 0 | 1 |  | 1 | 1.21
0x0059 | Air quality control pressure sensor activate zero calibration |  | 0 | 1 |  | 1 | 2.42
0x0060 | HC defrost pressure sensor activate zero calibration |  | 0 | 1 |  | 1 | 2.42
0x0061
0x0062
BMS I/O-modules
0x1000 | External operation I/O-module A, function |  | 0 | 1 |  | 0 | 1.20
0x1001 | External operation I/O-module A, temp sensor 1 function |  | 0 | 1 |  | 0 | 1.20
0x1002 | External operation I/O-module A, temp sensor 2 function |  | 0 | 1 |  | 0 | 1.20
0x1003 | External operation I/O-module A, digital output |  | 0 | 1 |  | 0 | 1.20
0x1004 | External operation I/O-module B, function |  | 0 | 1 |  | 0 | 1.20
0x1005 | External operation I/O-module B, temp sensor 1 function |  | 0 | 1 |  | 0 | 1.20
0x1006 | External operation I/O-module B, temp sensor 2 function |  | 0 | 1 |  | 0 | 1.20
0x1007 | External operation I/O-module B, digital output |  | 0 | 1 |  | 0 | 1.20
0x1008 | External operation I/O-module C, function |  | 0 | 1 |  | 0 | 1.20
0x1009 | External operation I/O-module C, temp sensor 1 function |  | 0 | 1 |  | 0 | 1.20
0x1010 | External operation I/O-module C, temp sensor 2 function |  | 0 | 1 |  | 0 | 1.20
0x1011 | External operation I/O-module C, digital output |  | 0 | 1 |  | 0 | 1.20

## Input Status
GOLD_E_F_Modbus_260227
Input Status. 1bit (RO).
Modbus | Name | Description | Min | Max | Unit | Default | Misc
Operation level/alarm
1x0001 | Operation active | Relay output status | 0 | 1
1x0002 | Damper operation active | Relay output status | 0 | 1
1x0003 | Low speed operation active | Low speed operation status | 0 | 1
1x0004 | High speed operation active | High speed operation status | 0 | 1
1x0005 | Intermittent night heat active |  | 0 | 1
1x0006 | Morning boost active |  | 0 | 1
1x0007 | Heating boost active |  | 0 | 1
1x0008 | Cooling boost active |  | 0 | 1
1x0009 | Summer night cool active |  | 0 | 1
1x0010
1x0011
1x0012
1x0013 | A-alarm active | Any alarm with priority class A active | 0 | 1
1x0014 | B-alarm active | Any alarm with priority class B active | 0 | 1
1x0015
1x0016
Heat exchange
1x0017 | HX operation active | HX status | 0 | 1
1x0018 | HX cool recovery active | HX cool recovery status | 0 | 1
1x0019 | HX defrost active | HX defrost status | 0 | 1
1x0020
1x0021
1x0022 | RHX speed monitor signal | RHX speed monitor status | 0 | 1
1x0023
1x0024
1x0025
1x0026
1x0027 | CHX-1 pump output | CHX-1 relay output status | 0 | 1
1x0028 | CHX-1 pump input | CHX-1 digital input status | 0 | 1
1x0029
1x0030 | Seasonal controlled temperature regulation indication |  | 0 | 1 |  |  | 2.46
AHU Coils
1x0031 | Season heat, extra regulation sequence allowed |  | 0 | 1
1x0032 | Season heat, re-heat allowed |  | 0 | 1
1x0033 | Extra regulation sequence 1, output | Relay output status | 0 | 1
1x0034 | Extra regulation sequence 1, power reduction active |  | 0 | 1
1x0035 | Extra regulation sequence 1, anti-frost regulation active |  | 0 | 1
1x0036 | Extra regulation sequence 1 combi coil input |  | 0 | 1 |  |  | 2.37
1x0037 | Extra regulation sequence 1 combi coil output |  | 0 | 1 |  |  | 2.37
1x0038 | Re-heat output | Relay output status | 0 | 1
1x0039 | Re-heat power reduction active |  | 0 | 1
1x0040 | Re-heat anti-frost regulation active |  | 0 | 1
1x0041
1x0042
1x0043 | Cool output 1 | Relay output status | 0 | 1
1x0044 | Cool output 2 | Relay output status | 0 | 1
1x0045
1x0046 | Extra regulation sequence 2 combi coil input |  | 0 | 1 |  |  | 2.37
1x0047 | Extra regulation sequence 2 combi coil output |  | 0 | 1 |  |  | 2.37
1x0048 | Extra regulation sequence 2, output | Relay output status | 0 | 1 |  |  | 1.13
1x0049 | Extra regulation sequence 2, power reduction active |  | 0 | 1 |  |  | 1.13
1x0050 | Extra regulation sequence 2, anti-frost regulation active |  | 0 | 1 |  |  | 1.13
Pre-heat
1x0051 | Pre-heat output | Relay output status | 0 | 1
1x0052 | Pre-heat power reduction active |  | 0 | 1
1x0053 | Pre-heat anti-frost regulation active |  | 0 | 1
1x0054
1x0055
Xzone
1x0056 | Xzone heat output | Relay output status | 0 | 1
1x0057 | Xzone heat power reduction active
1x0058 | Xzone heat anti-frost regulation active
1x0059
1x0060
1x0061
1x0062
1x0063 | Xzone cool output 1 | Relay output status | 0 | 1
1x0064 | Xzone cool output 2 | Relay output status | 0 | 1
1x0065 | Xzone combi coil module A input | Xzone combi coil module A digital input status | 0 | 1 |  |  | 2.43
1x0066 | Xzone combi coil module A output | Relay output status | 0 | 1 |  |  | 2.43
1x0067 | Xzone combi coil module B input | Xzone combi coil module B digital input status | 0 | 1 |  |  | 2.43
1x0068 | Xzone combi coil module B output | Relay output status | 0 | 1 |  |  | 2.43
1x0069
1x0070
Exhaust heat
1x0071
1x0072
1x0073
1x0074
1x0075 | Exhaust heat pump output | Relay output status | 0 | 1 |  |  | 2.43
1x0076 | Exhaust heat heating power reduction active |  | 0 | 1 |  |  | 2.43
1x0077 | Exhaust heat anti-frost regulation active |  | 0 | 1 |  |  | 2.43
1x0078
1x0079
1x0080
1x0081
1x0082
1x0083
1x0084
1x0085
1x0086
1x0087
1x0088
1x0089
1x0090
1x0091
1x0092
1x0093
1x0094
1x0095
1x0096
1x0097
1x0098
AYC
1x0099 | AYC heat pump output | Relay output status | 0 | 1
1x0100 | AYC heat pump input | Digital input status | 0 | 1
1x0101
1x0102
1x0103
1x0104 | AYC cool pump output | Relay output status | 0 | 1
1x0105 | AYC cool pump input | Digital input status | 0 | 1
1x0106
1x0107
1x0108
COOL DX
1x0109 | COOL DX compressor 1 output | Relay output status | 0 | 1
1x0110 | COOL DX compressor 1 input | Digital input status | 0 | 1
1x0111
1x0112
1x0113
1x0114
1x0115 | COOL DX compressor 2 output | Relay output status | 0 | 1
1x0116 | COOL DX compressor 2 input | Digital input status | 0 | 1
1x0117
1x0118
1x0119
1x0120
Wireless AP
1x0199 | Wireless AP active |  | 0 | 1 |  | 0 | 2.43
BMS I/O-modules
1x0200 | External operation I/O-module 3, digital input 1 |  | 0 | 1 |  |  | 1.20
1x0201 | External operation I/O-module 3, digital input 2 |  | 0 | 1 |  |  | 1.20
1x0202 | External operation I/O-module 3, digital output 1 |  | 0 | 1 |  |  | 1.20
1x0203 | External operation I/O-module 3, digital output 2 |  | 0 | 1 |  |  | 1.20
1x0204 | External operation I/O-module 6, digital input 1 |  | 0 | 1 |  |  | 1.20
1x0205 | External operation I/O-module 6, digital input 2 |  | 0 | 1 |  |  | 1.20
1x0206 | External operation I/O-module 6, digital output 1 |  | 0 | 1 |  |  | 1.20
1x0207 | External operation I/O-module 6, digital output 2 |  | 0 | 1 |  |  | 1.20
1x0208 | External operation I/O-module A, digital input |  | 0 | 1 |  |  | 1.20
1x0209 | External operation I/O-module B, digital input |  | 0 | 1 |  |  | 1.20
1x0210 | External operation I/O-module C, digital input |  | 0 | 1 |  |  | 1.20
Alarms
1x0501 | Active alarm 1 | Alarm 1:1 External fire alarm no. 1 tripped | 0 | 1
1x0502 | Active alarm 2 | Alarm 1:2 External fire alarm no. 2 tripped | 0 | 1
1x0503 | Active alarm 3 | Alarm 1:3 Internal fire alarm tripped | 0 | 1
1x0504 | Active alarm 4 |  | 0 | 1
1x0505 | Active alarm 5 |  | 0 | 1
1x0506 | Active alarm 6 |  | 0 | 1
1x0507 | Active alarm 7 |  | 0 | 1
1x0508 | Active alarm 8 |  | 0 | 1
1x0509 | Active alarm 9 |  | 0 | 1
1x0510 | Active alarm 10 |  | 0 | 1
1x0511 | Active alarm 11 |  | 0 | 1
1x0512 | Active alarm 12 |  | 0 | 1
1x0513 | Active alarm 13 |  | 0 | 1
1x0514 | Active alarm 14 |  | 0 | 1
1x0515 | Active alarm 15 |  | 0 | 1
1x0516 | Active alarm 16 | Alarm 2:1 External alarm no. 1 tripped | 0 | 1
1x0517 | Active alarm 17 | Alarm 2:2 External alarm no. 2 tripped | 0 | 1
1x0518 | Active alarm 18 |  | 0 | 1
1x0519 | Active alarm 19 |  | 0 | 1
1x0520 | Active alarm 20 |  | 0 | 1
1x0521 | Active alarm 21 |  | 0 | 1
1x0522 | Active alarm 22 |  | 0 | 1
1x0523 | Active alarm 23 |  | 0 | 1
1x0524 | Active alarm 24 |  | 0 | 1
1x0525 | Active alarm 25 |  | 0 | 1
1x0526 | Active alarm 26 |  | 0 | 1
1x0527 | Active alarm 27 |  | 0 | 1
1x0528 | Active alarm 28 |  | 0 | 1
1x0529 | Active alarm 29 |  | 0 | 1
1x0530 | Active alarm 30 |  | 0 | 1
1x0531 | Active alarm 31 | Alarm 3:1 Pre-heat, I/O-module no. 9 communication error | 0 | 1
1x0532 | Active alarm 32 | Alarm 3:2 Pre-heat, electrical heater overheat protection tripped | 0 | 1
1x0533 | Active alarm 33 | Alarm 3:3 Pre-heat, frost protection tripped | 0 | 1
1x0534 | Active alarm 34 | Alarm 3:4 Pre-heat, frost protection temperature sensor defective | 0 | 1
1x0535 | Active alarm 35 | Alarm 3:5 Pre-heat, temperature sensor defective | 0 | 1
1x0536 | Active alarm 36 | Alarm 3:6 Pre-heat, valve monitoring tripped | 0 | 1
1x0537 | Active alarm 37 | Alarm 3:7 Pre-heat, temperature below set point alarm limit | 0 | 1
1x0538 | Active alarm 38 | Alarm 3:8 Pre-heat, alarm input tripped | 0 | 1 |  |  | 1.10
1x0539 | Active alarm 39 |  | 0 | 1
1x0540 | Active alarm 40 |  | 0 | 1
1x0541 | Active alarm 41 |  | 0 | 1
1x0542 | Active alarm 42 |  | 0 | 1
1x0543 | Active alarm 43 |  | 0 | 1
1x0544 | Active alarm 44 |  | 0 | 1
1x0545 | Active alarm 45 |  | 0 | 1
1x0546 | Active alarm 46 | Alarm 4:1 Extra regulation sequence 1, I/O-module no. E communication error | 0 | 1 |  |  | 1.13
1x0547 | Active alarm 47 | Alarm 4:2 Extra regulation sequence 1, electrical heater overheat protection tripped | 0 | 1 |  |  | 1.13
1x0548 | Active alarm 48 | Alarm 4:3 Extra regulation sequence 1, frost protection tripped | 0 | 1 |  |  | 1.13
1x0549 | Active alarm 49 | Alarm 4:4 Extra regulation sequence 1, frost protection temperature sensor defective | 0 | 1 |  |  | 1.13
1x0550 | Active alarm 50 | Alarm 4:5 Extra regulation sequence 1, valve monitoring tripped | 0 | 1 |  |  | 1.13
1x0551 | Active alarm 51 | Alarm 4:6 Extra regulation sequence 1, alarm input tripped | 0 | 1 |  |  | 1.13
1x0552 | Active alarm 52 | Alarm 4:7 Extra regulation sequence 1, temperature protection from communication error | 0 | 1 |  |  | 1.13
1x0553 | Active alarm 53 | Alarm 4:8 Extra regulation sequence 1 combi coil temperature sensor defective | 0 | 1 |  |  | 1.26
1x0554 | Active alarm 54 | Alarm 4:9 Extra regulation sequence 2, I/O-module no. F communication error | 0 | 1 |  |  | 1.13
1x0555 | Active alarm 55 | Alarm 4:10 Extra regulation sequence 2, electrical heater overheat protection tripped | 0 | 1 |  |  | 1.13
1x0556 | Active alarm 56 | Alarm 4:11 Extra regulation sequence 2, frost protection tripped | 0 | 1 |  |  | 1.13
1x0557 | Active alarm 57 | Alarm 4:12 Extra regulation sequence 2, frost protection temperature sensor defective | 0 | 1 |  |  | 1.13
1x0558 | Active alarm 58 | Alarm 4:13 Extra regulation sequence 2, valve monitoring tripped | 0 | 1 |  |  | 1.13
1x0559 | Active alarm 59 | Alarm 4:14 Extra regulation sequence 2, alarm input tripped | 0 | 1 |  |  | 1.13
1x0560 | Active alarm 60 | Alarm 4:15 Extra regulation sequence 2 combi coil temperature sensor defective | 0 | 1 |  |  | 1.26
1x0561 | Active alarm 61 | Alarm 5:1 Re-heat, electrical heater over heat protection tripped | 0 | 1
1x0562 | Active alarm 62 | Alarm 5:2 Re-heat, frost protection tripped | 0 | 1
1x0563 | Active alarm 63 | Alarm 5:3 Re-heat, frost protection temperature sensor defective | 0 | 1
1x0564 | Active alarm 64 | Alarm 5:4 Re-heat, heat valve monitoring tripped | 0 | 1
1x0565 | Active alarm 65 | Alarm 5:5 Re-heat alarm input tripped | 0 | 1 |  |  | 1.27
1x0566 | Active alarm 66 |  | 0 | 1
1x0567 | Active alarm 67 |  | 0 | 1
1x0568 | Active alarm 68 |  | 0 | 1
1x0569 | Active alarm 69 |  | 0 | 1
1x0570 | Active alarm 70 |  | 0 | 1
1x0571 | Active alarm 71 |  | 0 | 1
1x0572 | Active alarm 72 |  | 0 | 1
1x0573 | Active alarm 73 |  | 0 | 1
1x0574 | Active alarm 74 |  | 0 | 1
1x0575 | Active alarm 75 |  | 0 | 1
1x0576 | Active alarm 76 | Alarm 6:1 Xzone, I/O-module no. A communication error | 0 | 1
1x0577 | Active alarm 77 | Alarm 6:2 Xzone, electrical heater overheat protection tripped | 0 | 1
1x0578 | Active alarm 78 | Alarm 6:3 Xzone, frost protection tripped | 0 | 1
1x0579 | Active alarm 79 | Alarm 6:4 Xzone, frost protection temperature sensor defective | 0 | 1
1x0580 | Active alarm 80 | Alarm 6:5 Xzone, supply air temperature sensor defective | 0 | 1
1x0581 | Active alarm 81 | Alarm 6:6 Xzone, heat valve monitoring tripped | 0 | 1
1x0582 | Active alarm 82 | Alarm 6:7 Xzone, supply air temperature below set point alarm limit | 0 | 1
1x0583 | Active alarm 83 | Alarm 6:8 Xzone, supply air temperature above set point alarm limit | 0 | 1
1x0584 | Active alarm 84 | Alarm 6:9 Xzone, heat alarm input tripped | 0 | 1 |  |  | 1.10
1x0585 | Active alarm 85 | Alarm 6:10 Xzone combi coil module A temperature sensor defective | 0 | 1 |  |  | 2.43
1x0586 | Active alarm 86 | Alarm 6:11 Xzone temperature protection, I/O-module no. 9 com. Error | 0 | 1 |  |  | 2.43
1x0587 | Active alarm 87 |  | 0 | 1
1x0588 | Active alarm 88 |  | 0 | 1
1x0589 | Active alarm 89 |  | 0 | 1
1x0590 | Active alarm 90 |  | 0 | 1
1x0591 | Active alarm 91 | Alarm 7:1 Xzone, I/O-module no. B communication error | 0 | 1
1x0592 | Active alarm 92 | Alarm 7:2 Xzone, extract air temperature sensor defective | 0 | 1
1x0593 | Active alarm 93 | Alarm 7:3 Xzone, cool valve monitoring tripped | 0 | 1
1x0594 | Active alarm 94 | Alarm 7:4 Xzone, extract air temperature below alarm limit | 0 | 1
1x0595 | Active alarm 95 | Alarm 7:5 Xzone, cool alarm input 1 tripped | 0 | 1 |  |  | 1.10
1x0596 | Active alarm 96 | Alarm 7:6 Xzone, cool alarm input 2 tripped | 0 | 1 |  |  | 1.10
1x0597 | Active alarm 97 | Alarm 7:7 Xzone combi coil module B temperature sensor defective | 0 | 1 |  |  | 2.43
1x0598 | Active alarm 98 |  | 0 | 1
1x0599 | Active alarm 99 |  | 0 | 1
1x0600 | Active alarm 100 |  | 0 | 1
1x0601 | Active alarm 101 |  | 0 | 1
1x0602 | Active alarm 102 |  | 0 | 1
1x0603 | Active alarm 103 |  | 0 | 1
1x0604 | Active alarm 104 |  | 0 | 1
1x0605 | Active alarm 105 |  | 0 | 1
1x0606 | Active alarm 106 |  | 0 | 1
1x0607 | Active alarm 107 |  | 0 | 1
1x0608 | Active alarm 108 |  | 0 | 1
1x0609 | Active alarm 109 |  | 0 | 1
1x0610 | Active alarm 110 | Alarm 8:5 Cool valve monitoring tripped | 0 | 1
1x0611 | Active alarm 111 | Alarm 8:6 Cool alarm input 1 tripped | 0 | 1 |  |  | 1.27
1x0612 | Active alarm 112 | Alarm 8:7 Cool alarm input 2 tripped | 0 | 1 |  |  | 1.27
1x0613 | Active alarm 113 |  | 0 | 1
1x0614 | Active alarm 114 |  | 0 | 1
1x0615 | Active alarm 115 |  | 0 | 1
1x0616 | Active alarm 116 |  | 0 | 1
1x0617 | Active alarm 117 |  | 0 | 1
1x0618 | Active alarm 118 |  | 0 | 1
1x0619 | Active alarm 119 |  | 0 | 1
1x0620 | Active alarm 120 |  | 0 | 1
1x0621 | Active alarm 121 | Alarm 9:1 Exhaust heat I/O-module no. 4 com error | 0 | 1 |  |  | 2.43
1x0622 | Active alarm 122 | Alarm 9:2 Exhaust heat electrical heater overheat protection tripped | 0 | 1 |  |  | 2.43
1x0623 | Active alarm 123 | Alarm 9:3 Exhaust heat frost protection tripped | 0 | 1 |  |  | 2.43
1x0624 | Active alarm 124 | Alarm 9:4 Exhaust heat frost protection temperature sensor defective | 0 | 1 |  |  | 2.43
1x0625 | Active alarm 125 | Alarm 9:5 Exhaust heat temperature sensor defective | 0 | 1 |  |  | 2.43
1x0626 | Active alarm 126 | Alarm 9:6 Exhaust heat valve monitoring tripped | 0 | 1 |  |  | 2.43
1x0627 | Active alarm 127 | Alarm 9:7 Exhaust heat temperature below set point alarm limit | 0 | 1 |  |  | 2.43
1x0628 | Active alarm 128 | Alarm 9:8 Exhaust heat alarm input tripped | 0 | 1 |  |  | 2.43
1x0629 | Active alarm 129 |  | 0 | 1
1x0630 | Active alarm 130 |  | 0 | 1
1x0631 | Active alarm 131 |  | 0 | 1
1x0632 | Active alarm 132 |  | 0 | 1
1x0633 | Active alarm 133 |  | 0 | 1
1x0634 | Active alarm 134 |  | 0 | 1
1x0635 | Active alarm 135 |  | 0 | 1
1x0636 | Active alarm 136 | Alarm 10:1 Supply air temperature sensor defective | 0 | 1
1x0637 | Active alarm 137 | Alarm 10:2 Supply air temperature sensor for density compensation defective | 0 | 1
1x0638 | Active alarm 138 | Alarm 10:3 Extract air temperature sensor defective | 0 | 1
1x0639 | Active alarm 139 | Alarm 10:4 Extract air temperature sensor for density compensation defective | 0 | 1
1x0640 | Active alarm 140 | Alarm 10:5 Extract air temperature sensor for heat exchanger defrosting defective | 0 | 1
1x0641 | Active alarm 141 | Alarm 10:6 Extract air temperature sensor for density compensation in SD air handling unit defective | 0 | 1
1x0642 | Active alarm 142 | Alarm 10:7 Extract air duct temperature sensor defective | 0 | 1 |  |  | 1.13
1x0643 | Active alarm 143 |  | 0 | 1
1x0644 | Active alarm 144 |  | 0 | 1
1x0645 | Active alarm 145 | Alarm 10:10 Outdoor air temperature sensor defective | 0 | 1
1x0646 | Active alarm 146 |  | 0 | 1
1x0647 | Active alarm 147 |  | 0 | 1
1x0648 | Active alarm 148 |  | 0 | 1
1x0649 | Active alarm 149 |  | 0 | 1
1x0650 | Active alarm 150 |  | 0 | 1
1x0651 | Active alarm 151 | Alarm 11:1 Room temperature sensor no. 1 defective | 0 | 1
1x0652 | Active alarm 152 | Alarm 11:2 Room temperature sensor no. 2 defective | 0 | 1
1x0653 | Active alarm 153 | Alarm 11:3 Room temperature sensor no. 3 defective | 0 | 1
1x0654 | Active alarm 154 | Alarm 11:4 Room temperature sensor no. 4 defective | 0 | 1
1x0655 | Active alarm 155 | Alarm 11:5 Xzone, room temperature sensor no. 5 defective | 0 | 1
1x0656 | Active alarm 156 | Alarm 11:6 Xzone, room temperature sensor no. 6 defective | 0 | 1
1x0657 | Active alarm 157 | Alarm 11:7 Xzone, room temperature sensor no. 7 defective | 0 | 1
1x0658 | Active alarm 158 | Alarm 11:8 Xzone, room temperature sensor no. 8 defective | 0 | 1
1x0659 | Active alarm 159 | Alarm 11:9 Outdoor temperature sensor no. A defective | 0 | 1
1x0660 | Active alarm 160 | Alarm 11:10 Outdoor temperature sensor no. B defective | 0 | 1
1x0661 | Active alarm 161 | Alarm 11:11 Outdoor temperature sensor no. C defective | 0 | 1
1x0662 | Active alarm 162 | Alarm 11:12 Outdoor temperature sensor no. D defective | 0 | 1
1x0663 | Active alarm 163 | Alarm 11:13 Room temperature from communication error | 0 | 1
1x0664 | Active alarm 164 | Alarm 11:14 Xzone, room temperature from communication error | 0 | 1
1x0665 | Active alarm 165 | Alarm 11:15 Outdoor temperature from communication error | 0 | 1
1x0666 | Active alarm 166 | Alarm 12:1 Supply air temperature below set point alarm limit | 0 | 1
1x0667 | Active alarm 167 | Alarm 12:2 Supply air temperature above set point alarm limit | 0 | 1
1x0668 | Active alarm 168 |  | 0 | 1
1x0669 | Active alarm 169 |  | 0 | 1
1x0670 | Active alarm 170 |  | 0 | 1
1x0671 | Active alarm 171 | Alarm 12:6 Extract air temperature below alarm limit | 0 | 1
1x0672 | Active alarm 172 |  | 0 | 1
1x0673 | Active alarm 173 |  | 0 | 1
1x0674 | Active alarm 174 |  | 0 | 1
1x0675 | Active alarm 175 |  | 0 | 1
1x0676 | Active alarm 176 | Alarm 12:11 temperature guard below Alarm limit | 0 | 1
1x0677 | Active alarm 177 |  | 0 | 1
1x0678 | Active alarm 178 | Alarm 12:13 Heat exchange efficiency below alarm limit | 0 | 1 |  |  | 1.21
1x0679 | Active alarm 179 |  | 0 | 1
1x0680 | Active alarm 180 |  | 0 | 1
1x0681 | Active alarm 181 | Alarm 13:1 Humidification, I/O-module no. 4 communication error | 0 | 1
1x0682 | Active alarm 182 | Alarm 13:2 Supply air humidity sensor defective | 0 | 1
1x0683 | Active alarm 183 | Alarm 13:3 Extract air humidity sensor defective | 0 | 1
1x0684 | Active alarm 184 | Alarm 13:4 Exhaust air humidity sensor defective | 0 | 1 |  |  | 1.21
1x0685 | Active alarm 185 | Alarm 13:5 Outdoor air humidity sensor defective | 0 | 1 |  |  | 2.36
1x0686 | Active alarm 186 | Alarm 13:6 Room humidity sensor defective | 0 | 1 |  |  | 2.36
1x0687 | Active alarm 187 |  | 0 | 1
1x0688 | Active alarm 188 |  | 0 | 1
1x0689 | Active alarm 189 | Alarm 13:9 Humidifier alarm output tripped | 0 | 1
1x0690 | Active alarm 190 |  | 0 | 1
1x0691 | Active alarm 191 | Alarm 13:11 VOC sensor, communication error | 0 | 1
1x0692 | Active alarm 192 | Alarm 13:12 VOC sensor, internal communication error | 0 | 1
1x0693 | Active alarm 193 | Alarm 13:13 VOC sensor, internal error | 0 | 1 |  |  | 1.10
1x0694 | Active alarm 194 | Alarm 13:14 VOC sensor, level below/above set point alarm limit | 0 | 1 |  |  | 1.10
1x0695 | Active alarm 195 |  | 0 | 1
1x0696 | Active alarm 196 | Alarm 14:1 Re-heat liquid flow measurement I/O-module no. 6 com. error | 0 | 1 |  |  | 2.47
1x0697 | Active alarm 197 | Alarm 14:2 Re-heat liquid flow measurement temp. sensor no. 1 defective | 0 | 1 |  |  | 2.47
1x0698 | Active alarm 198 | Alarm 14:3 Re-heat liquid flow measurement temp. sensor no. 2 defective | 0 | 1 |  |  | 2.47
1x0699 | Active alarm 199 | Alarm 14:4 Re-heat liquid flow measurement valve leakage | 0 | 1 |  |  | 2.47
1x0700 | Active alarm 200 | Alarm 14:5 Re-heat liquid flow measurement flow sensor defective | 0 | 1 |  |  | 2.47
1x0701 | Active alarm 201 |  | 0 | 1 |  |  | 2.47
1x0702 | Active alarm 202 |  | 0 | 1 |  |  | 2.47
1x0703 | Active alarm 203 | Alarm 14:8 Cool liquid flow measurement I/O-module no. 7 com. error | 0 | 1 |  |  | 2.47
1x0704 | Active alarm 204 | Alarm 14:9 Cool liquid flow measurement temp. sensor no. 1 defective | 0 | 1 |  |  | 2.47
1x0705 | Active alarm 205 | Alarm 14:10 Cool liquid flow measurement temp. sensor no. 2 defective | 0 | 1 |  |  | 2.47
1x0706 | Active alarm 206 | Alarm 14:11 Cool liquid flow measurement valve leakage | 0 | 1 |  |  | 2.47
1x0707 | Active alarm 207 | Alarm 14:12 Cool liquid flow measurement flow sensor defective | 0 | 1 |  |  | 2.47
1x0708 | Active alarm 208 |  | 0 | 1
1x0709 | Active alarm 209 |  | 0 | 1
1x0710 | Active alarm 210 |  | 0 | 1
1x0711 | Active alarm 211 | Alarm 15:1 Plate heat exchanger, I/O-module no. 2 communication error | 0 | 1
1x0712 | Active alarm 212 | Alarm 15:2 Plate heat exchanger, temperature sensor no. 1 defective | 0 | 1
1x0713 | Active alarm 213 | Alarm 15:3 Plate heat exchanger, temperature sensor no. 2 defective | 0 | 1
1x0714 | Active alarm 214 | Alarm 15:4 Plate heat exchanger, damper monitor tripped | 0 | 1
1x0715 | Active alarm 215 |  | 0 | 1
1x0716 | Active alarm 216 | Alarm 15:6 Plate heat exchanger bypass damper 4A monitor tripped | 0 | 1 |  |  | 2.43
1x0717 | Active alarm 217 | Alarm 15:7 Plate heat exchanger, I/O-module no. 3 communication error | 0 | 1 |  |  | 1.13
1x0718 | Active alarm 218 | Alarm 15:8 Plate heat exchanger, bypass damper monitor tripped | 0 | 1 |  |  | 1.13
1x0719 | Active alarm 219 | Alarm 15:9 Plate heat exchanger, damper no. 1 monitor tripped | 0 | 1 |  |  | 1.13
1x0720 | Active alarm 220 | Alarm 15:10 Plate heat exchanger, damper no. 2 monitor tripped | 0 | 1 |  |  | 1.13
1x0721 | Active alarm 221 | Alarm 15:11 Plate heat exchanger, I/O-module no. 3 communication error | 0 | 1 |  |  | 1.13
1x0722 | Active alarm 222 | Alarm 15:12 Plate heat exchanger, bypass damper monitor tripped | 0 | 1 |  |  | 1.13
1x0723 | Active alarm 223 | Alarm 15:13 Plate counter flow heat exchanger, defrost pressure above alarm limit | 0 | 1 |  |  | 1.21
1x0724 | Active alarm 224 | Alarm 15:14 Plate heat exchanger, defrost pressure sensor no. C communication error | 0 | 1 |  |  | 1.13
1x0725 | Active alarm 225 | Alarm 15:15 Plate heat exchanger, defrost pressure above alarm limit | 0 | 1 |  |  | 1.13
1x0726 | Active alarm 226 | Alarm 16:1 Coil heat exchanger, I/O-module no. 1 communication error | 0 | 1
1x0727 | Active alarm 227 | Alarm 16:2 Coil heat exchanger, temperature sensor defective | 0 | 1
1x0728 | Active alarm 228 | Alarm 16:3 Coil heat exchanger, valve monitor tripped | 0 | 1
1x0729 | Active alarm 229 | Alarm 16:4 Coil heat exchanger, pump monitor tripped | 0 | 1
1x0730 | Active alarm 230 | Alarm 16:5 Coil heat exchanger, I/O-module no. C communication error | 0 | 1 |  |  | 1.18
1x0731 | Active alarm 231 | Alarm 16:6 Coil heat exchanger, pressure sensor defective | 0 | 1 |  |  | 1.18
1x0732 | Active alarm 232 | Alarm 16:7 Coil heat exchanger, low pressure brine circuit | 0 | 1 |  |  | 1.18
1x0733 | Active alarm 233 | Alarm 16:8 Coil heat exchanger pressure below alarm limit | 0 | 1 |  |  | 1.27
1x0734 | Active alarm 234 |  | 0 | 1
1x0735 | Active alarm 235 |  | 0 | 1
1x0736 | Active alarm 236 |  | 0 | 1
1x0737 | Active alarm 237 |  | 0 | 1
1x0738 | Active alarm 238 |  | 0 | 1
1x0739 | Active alarm 239 |  | 0 | 1
1x0740 | Active alarm 240 |  | 0 | 1
1x0741 | Active alarm 241 | Alarm 17:1 Rotary heat exchanger, motor controller communication error | 0 | 1
1x0742 | Active alarm 242 | Alarm 17:2 Rotary heat exchanger, defrost pressure sensor no. 7 communication error | 0 | 1
1x0743 | Active alarm 243 | Alarm 17:3 Rotary heat exchanger, defrost pressure above alarm limit | 0 | 1
1x0744 | Active alarm 244 | Alarm 17:4 Rotary heat exchanger, speed monitor tripped | 0 | 1
1x0745 | Active alarm 245 | Alarm 17:5 Rotary heat exchanger, motor controller over current | 0 | 1
1x0746 | Active alarm 246 | Alarm 17:6 Rotary heat exchanger, motor controller under voltage | 0 | 1
1x0747 | Active alarm 247 | Alarm 17:7 Rotary heat exchanger, motor controller over voltage | 0 | 1
1x0748 | Active alarm 248 | Alarm 17:8 Rotary heat exchanger, motor controller over temperature | 0 | 1
1x0749 | Active alarm 249 | Alarm 17:9 Rotary heat exchanger, motor controller start error | 0 | 1
1x0750 | Active alarm 250 | Alarm 17:10 Rotary heat exchanger, motor controller internal error | 0 | 1 |  |  | 1.32
1x0751 | Active alarm 251 | Alarm 17:11 Rotary heat exchanger, motor controller phase error | 0 | 1 |  |  | 1.32
1x0752 | Active alarm 252 | Alarm 17:12 Rotary heat exchanger, motor controller internal memory error | 0 | 1 |  |  | 1.32
1x0753 | Active alarm 253 | Alarm 17:13 Rotary heat exchanger, motor controller current reduction | 0 | 1 |  |  | 1.32
1x0754 | Active alarm 254 | Alarm 17:14 Rotary heat exchanger, motor controller internal com. error | 0 | 1 |  |  | 1.32
1x0755 | Active alarm 255 | Alarm 17:15 Rotary heat exchanger, I/O-module com. error | 0 | 1 |  |  | 1.32
1x0756 | Active alarm 256 | Alarm 18:1 AYC, I/O-module no. 7 communication error | 0 | 1
1x0757 | Active alarm 257 | Alarm 18:2 AYC heat, temperature sensor defective | 0 | 1
1x0758 | Active alarm 258 | Alarm 18:3 AYC heat, valve monitor tripped | 0 | 1
1x0759 | Active alarm 259 | Alarm 18:4 AYC heat, pump monitor tripped | 0 | 1
1x0760 | Active alarm 260 | Alarm 18:5 AYC heat, temperature below set point alarm limit | 0 | 1
1x0761 | Active alarm 261 | Alarm 18:6 AYC heat, temperature above set point alarm limit | 0 | 1
1x0762 | Active alarm 262 |  | 0 | 1
1x0763 | Active alarm 263 |  | 0 | 1
1x0764 | Active alarm 264 | Alarm 18:9 AYC cool, temperature sensor defective | 0 | 1
1x0765 | Active alarm 265 | Alarm 18:10 AYC cool, valve monitor tripped | 0 | 1
1x0766 | Active alarm 266 | Alarm 18:11 AYC cool, pump monitor tripped | 0 | 1
1x0767 | Active alarm 267 | Alarm 18:12 AYC cool, temperature below set point alarm limit | 0 | 1
1x0768 | Active alarm 268 | Alarm 18:13 AYC cool, temperature above set point alarm limit | 0 | 1
1x0769 | Active alarm 269 |  | 0 | 1
1x0770 | Active alarm 270 |  | 0 | 1
1x0771 | Active alarm 271 | Alarm 19:1 Rotary heat exchanger, AQC pressure sensor no. E com. error | 0 | 1 |  |  | 1.32
1x0772 | Active alarm 272 | Alarm 19:2 Rotary heat exchanger, AQC pressure below set point alarm limit | 0 | 1 |  |  | 1.32
1x0773 | Active alarm 273 | Alarm 19:3 Rotary heat exchanger, AQC damper monitoring tripped | 0 | 1 |  |  | 1.32
1x0774 | Active alarm 274 |  | 0 | 1
1x0775 | Active alarm 275 |  | 0 | 1
1x0776 | Active alarm 276 |  | 0 | 1
1x0777 | Active alarm 277 |  | 0 | 1
1x0778 | Active alarm 278 |  | 0 | 1
1x0779 | Active alarm 279 |  | 0 | 1
1x0780 | Active alarm 280 |  | 0 | 1
1x0781 | Active alarm 281 |  | 0 | 1
1x0782 | Active alarm 282 |  | 0 | 1
1x0783 | Active alarm 283 |  | 0 | 1
1x0784 | Active alarm 284 |  | 0 | 1
1x0785 | Active alarm 285 |  | 0 | 1
1x0786 | Active alarm 286 |  | 0 | 1
1x0787 | Active alarm 287 |  | 0 | 1
1x0788 | Active alarm 288 |  | 0 | 1
1x0789 | Active alarm 289 |  | 0 | 1
1x0790 | Active alarm 290 |  | 0 | 1
1x0791 | Active alarm 291 |  | 0 | 1
1x0792 | Active alarm 292 |  | 0 | 1
1x0793 | Active alarm 293 |  | 0 | 1
1x0794 | Active alarm 294 |  | 0 | 1
1x0795 | Active alarm 295 |  | 0 | 1
1x0796 | Active alarm 296 |  | 0 | 1
1x0797 | Active alarm 297 |  | 0 | 1
1x0798 | Active alarm 298 |  | 0 | 1
1x0799 | Active alarm 299 |  | 0 | 1
1x0800 | Active alarm 300 |  | 0 | 1
1x0801 | Active alarm 301 | Alarm 21:1 COOL DX, I/O-module no. 2 communication error | 0 | 1
1x0802 | Active alarm 302 | Alarm 21:2 COOL DX, compressor no. 1 low pressure sensor defective | 0 | 1
1x0803 | Active alarm 303 | Alarm 21:3 COOL DX, compressor no. 1 low pressure below alarm limit | 0 | 1
1x0804 | Active alarm 304 | Alarm 21:4 COOL DX, compressor no. 1 high pressure sensor defective | 0 | 1
1x0805 | Active alarm 305 | Alarm 21:5 COOL DX, compressor no. 1 high pressure above alarm limit | 0 | 1
1x0806 | Active alarm 306 | Alarm 21:6 COOL DX, compressor no. 1 monitor tripped | 0 | 1
1x0807 | Active alarm 307 | Alarm 21:7 COOL DX, compressor no. 1 restart error | 0 | 1
1x0808 | Active alarm 308 | Alarm 21:8 COOL DX, compressor no. 2 low pressure sensor defective | 0 | 1
1x0809 | Active alarm 309 | Alarm 21:9 COOL DX, compressor no. 2 low pressure below alarm limit | 0 | 1
1x0810 | Active alarm 310 | Alarm 21:10 COOL DX, compressor no. 2 high pressure sensor defective | 0 | 1
1x0811 | Active alarm 311 | Alarm 21:11 COOL DX, compressor no. 2 high pressure above alarm limit | 0 | 1
1x0812 | Active alarm 312 | Alarm 21:12 COOL DX, compressor no. 2 monitor tripped | 0 | 1
1x0813 | Active alarm 313 | Alarm 21:13 COOL DX, compressor no. 2 restart error | 0 | 1
1x0814 | Active alarm 314 | Alarm 21:14 COOL DX, outdoor air temperature sensor defective | 0 | 1
1x0815 | Active alarm 315 | Alarm 21:15 COOL DX phase sequence error or supply voltage missing | 0 | 1
1x0816 | Active alarm 316 | Alarm 22:1 Xzone heat liquid flow measurement I/O-module no. D com. error | 0 | 1 |  |  | 2.47
1x0817 | Active alarm 317 | Alarm 22:2 Xzone heat liquid flow measurement temp. sensor no. 1 defective | 0 | 1 |  |  | 2.47
1x0818 | Active alarm 318 | Alarm 22:3 Xzone heat liquid flow measurement temp. sensor no. 2 defective | 0 | 1 |  |  | 2.47
1x0819 | Active alarm 319 | Alarm 22:4 Xzone heat liquid flow measurement valve leakage | 0 | 1 |  |  | 2.47
1x0820 | Active alarm 320 | Alarm 22:5 Xzone heat liquid flow measurement flow sensor defective | 0 | 1 |  |  | 2.47
1x0821 | Active alarm 321 |  | 0 | 1 |  |  | 2.47
1x0822 | Active alarm 322 |  | 0 | 1 |  |  | 2.47
1x0823 | Active alarm 323 | Alarm 22:8 Xzone cool liquid flow measurement I/O-module no. E com. error | 0 | 1 |  |  | 2.47
1x0824 | Active alarm 324 | Alarm 22:9 Xzone cool liquid flow measurement temp. sensor no. 1 defective | 0 | 1 |  |  | 2.47
1x0825 | Active alarm 325 | Alarm 22:10 Xzone cool liquid flow measurement temp. sensor no. 2 defective | 0 | 1 |  |  | 2.47
1x0826 | Active alarm 326 | Alarm 22:11 Xzone cool liquid flow measurement valve leakage | 0 | 1 |  |  | 2.47
1x0827 | Active alarm 327 | Alarm 22:12 Xzone cool liquid flow measurement flow sensor defective | 0 | 1 |  |  | 2.47
1x0828 | Active alarm 328 |  | 0 | 1
1x0829 | Active alarm 329 |  | 0 | 1
1x0830 | Active alarm 330 |  | 0 | 1
1x0831 | Active alarm 331 | Alarm 23:1 SMART Link, communication error | 0 | 1
1x0832 | Active alarm 332 | Alarm 23:2 SMART Link, alarm level 1 tripped | 0 | 1
1x0833 | Active alarm 333 | Alarm 23:3 SMART Link, alarm level 2 tripped | 0 | 1
1x0834 | Active alarm 334 | Alarm 23:4 SMART Link, alarm level 3 tripped | 0 | 1
1x0835 | Active alarm 335 |  | 0 | 1
1x0836 | Active alarm 336 |  | 0 | 1
1x0837 | Active alarm 337 |  | 0 | 1
1x0838 | Active alarm 338 |  | 0 | 1
1x0839 | Active alarm 339 |  | 0 | 1
1x0840 | Active alarm 340 | Alarm 23:10 AQUA Link, I/O-module no. 5 communication error | 0 | 1
1x0841 | Active alarm 341 | Alarm 23:11 AQUA Link, pump monitor tripped | 0 | 1
1x0842 | Active alarm 342 |  | 0 | 1
1x0843 | Active alarm 343 |  | 0 | 1
1x0844 | Active alarm 344 |  | 0 | 1
1x0845 | Active alarm 345 |  | 0 | 1
1x0846 | Active alarm 346 | Alarm 24:1 SMART Link, no. 1 communication error | 0 | 1
1x0847 | Active alarm 347 | Alarm 24:2 SMART Link, no. 1 alarm tripped | 0 | 1
1x0848 | Active alarm 348 |  | 0 | 1
1x0849 | Active alarm 349 | Alarm 24:4 SMART Link, no. 2 communication error | 0 | 1
1x0850 | Active alarm 350 | Alarm 24:5 SMART Link, no. 2 alarm tripped | 0 | 1
1x0851 | Active alarm 351 |  | 0 | 1
1x0852 | Active alarm 352 | Alarm 24:7 SMART Link, no. 3 communication error | 0 | 1
1x0853 | Active alarm 353 | Alarm 24:8 SMART Link, no. 3 alarm tripped | 0 | 1
1x0854 | Active alarm 354 |  | 0 | 1
1x0855 | Active alarm 355 | Alarm 24:10 SMART Link, no. 4 communication error | 0 | 1
1x0856 | Active alarm 356 | Alarm 24:11 SMART Link, no. 4 alarm tripped | 0 | 1
1x0857 | Active alarm 357 |  | 0 | 1
1x0858 | Active alarm 358 | Alarm 24:13 SMART Link supply air flow below alarm limit | 0 | 1 |  |  | 1.25
1x0859 | Active alarm 359 |  | 0 | 1
1x0860 | Active alarm 360 |  | 0 | 1
1x0861 | Active alarm 361 | Alarm 25:1 SMART Link+, cooling circuit A com. error | 0 | 1 |  |  | 1.32
1x0862 | Active alarm 362 | Alarm 25:2 SMART Link+, cooling circuit B com. error | 0 | 1 |  |  | 1.32
1x0863 | Active alarm 363 | Alarm 25:3 SMART Link+, heating circuit A com. error | 0 | 1 |  |  | 1.32
1x0864 | Active alarm 364 | Alarm 25:4 SMART Link+, heating circuit B com. error | 0 | 1 |  |  | 1.32
1x0865 | Active alarm 365 |  | 0 | 1
1x0866 | Active alarm 366 |  | 0 | 1
1x0867 | Active alarm 367 |  | 0 | 1
1x0868 | Active alarm 368 |  | 0 | 1
1x0869 | Active alarm 369 |  | 0 | 1
1x0870 | Active alarm 370 |  | 0 | 1
1x0871 | Active alarm 371 |  | 0 | 1
1x0872 | Active alarm 372 |  | 0 | 1
1x0873 | Active alarm 373 |  | 0 | 1
1x0874 | Active alarm 374 |  | 0 | 1
1x0875 | Active alarm 375 |  | 0 | 1
1x0876 | Active alarm 376 | Alarm 26:1 Pre-filter, supply air pressure sensor no.8 communication error | 0 | 1
1x0877 | Active alarm 377 | Alarm 26:2 Pre-filter, supply air dirty | 0 | 1
1x0878 | Active alarm 378 |  | 0 | 1
1x0879 | Active alarm 379 |  | 0 | 1
1x0880 | Active alarm 380 |  | 0 | 1
1x0881 | Active alarm 381 |  | 0 | 1
1x0882 | Active alarm 382 | Alarm 26:7 Pre-filter, extract air pressure sensor no.9 communication error | 0 | 1
1x0883 | Active alarm 383 | Alarm 26:8 Pre-filter, extract air dirty | 0 | 1
1x0884 | Active alarm 384 |  | 0 | 1
1x0885 | Active alarm 385 |  | 0 | 1
1x0886 | Active alarm 386 |  | 0 | 1
1x0887 | Active alarm 387 |  | 0 | 1
1x0888 | Active alarm 388 |  | 0 | 1
1x0889 | Active alarm 389 |  | 0 | 1
1x0890 | Active alarm 390 |  | 0 | 1
1x0891 | Active alarm 391 | Alarm 27:1 Air handling unit filter, supply air pressure sensor no. 3/4 communication error | 0 | 1
1x0892 | Active alarm 392 | Alarm 27:2 Air handling unit filter, supply air dirty | 0 | 1
1x0893 | Active alarm 393 |  | 0 | 1
1x0894 | Active alarm 394 |  | 0 | 1
1x0895 | Active alarm 395 |  | 0 | 1
1x0896 | Active alarm 396 |  | 0 | 1
1x0897 | Active alarm 397 | Alarm 27:7 Air handling unit filter, extract air pressure sensor no. 3/4 communication error | 0 | 1
1x0898 | Active alarm 398 | Alarm 27:8 Air handling unit filter, extract air dirty | 0 | 1
1x0899 | Active alarm 399 |  | 0 | 1
1x0900 | Active alarm 400 |  | 0 | 1
1x0901 | Active alarm 401 |  | 0 | 1
1x0902 | Active alarm 402 |  | 0 | 1
1x0903 | Active alarm 403 |  | 0 | 1
1x0904 | Active alarm 404 |  | 0 | 1
1x0905 | Active alarm 405 |  | 0 | 1
1x0906 | Active alarm 406 | Alarm 28:1 End filter, supply air pressure sensor no. A communication error | 0 | 1
1x0907 | Active alarm 407 | Alarm 28:2 End filter, supply air dirty | 0 | 1
1x0908 | Active alarm 408 |  | 0 | 1
1x0909 | Active alarm 409 |  | 0 | 1
1x0910 | Active alarm 410 |  | 0 | 1
1x0911 | Active alarm 411 |  | 0 | 1
1x0912 | Active alarm 412 |  | 0 | 1
1x0913 | Active alarm 413 |  | 0 | 1
1x0914 | Active alarm 414 |  | 0 | 1
1x0915 | Active alarm 415 |  | 0 | 1
1x0916 | Active alarm 416 |  | 0 | 1
1x0917 | Active alarm 417 |  | 0 | 1
1x0918 | Active alarm 418 |  | 0 | 1
1x0919 | Active alarm 419 |  | 0 | 1
1x0920 | Active alarm 420 |  | 0 | 1
1x0921 | Active alarm 421 | Alarm 29:1 Energy monitoring pulse counter com. Error | 0 | 1 |  |  | 2.42
1x0922 | Active alarm 422 |  | 0 | 1
1x0923 | Active alarm 423 |  | 0 | 1
1x0924 | Active alarm 424 |  | 0 | 1
1x0925 | Active alarm 425 |  | 0 | 1
1x0926 | Active alarm 426 |  | 0 | 1
1x0927 | Active alarm 427 |  | 0 | 1
1x0928 | Active alarm 428 |  | 0 | 1
1x0929 | Active alarm 429 |  | 0 | 1
1x0930 | Active alarm 430 |  | 0 | 1
1x0931 | Active alarm 431 |  | 0 | 1
1x0932 | Active alarm 432 |  | 0 | 1
1x0933 | Active alarm 433 |  | 0 | 1
1x0934 | Active alarm 434 |  | 0 | 1
1x0935 | Active alarm 435 |  | 0 | 1
1x0936 | Active alarm 436 | Alarm 30:1 Air flow measurement, supply air pressure sensor no. 1/2 communication error | 0 | 1
1x0937 | Active alarm 437 | Alarm 30:2 Air flow measurement, supply air flow below set point alarm limit | 0 | 1
1x0938 | Active alarm 438 | Alarm 30:3 Air flow measurement, supply air flow above set point alarm limit | 0 | 1
1x0939 | Active alarm 439 |  | 0 | 1
1x0940 | Active alarm 440 |  | 0 | 1
1x0941 | Active alarm 441 | Alarm 30:6 Air flow measurement, extract air pressure sensor no. 1/2 communication error | 0 | 1
1x0942 | Active alarm 442 | Alarm 30:7 Air flow measurement, extract air flow below set point alarm limit | 0 | 1
1x0943 | Active alarm 443 | Alarm 30:8 Air flow measurement, extract air flow above set point alarm limit | 0 | 1
1x0944 | Active alarm 444 |  | 0 | 1
1x0945 | Active alarm 445 |  | 0 | 1
1x0946 | Active alarm 446 | Alarm 30:11 Air flow measurement, carry over control pressure sensor no. B communication error | 0 | 1
1x0947 | Active alarm 447 |  | 0 | 1
1x0948 | Active alarm 448 |  | 0 | 1
1x0949 | Active alarm 449 |  | 0 | 1
1x0950 | Active alarm 450 |  | 0 | 1
1x0951 | Active alarm 451 | Alarm 31:1 Pressure regulation, supply air pressure sensor no. 5 communication error | 0 | 1
1x0952 | Active alarm 452 | Alarm 31:2 Pressure regulation, supply air pressure below set point alarm limit | 0 | 1
1x0953 | Active alarm 453 | Alarm 31:3 Pressure regulation, supply air pressure above set point alarm limit | 0 | 1
1x0954 | Active alarm 454 |  | 0 | 1
1x0955 | Active alarm 455 |  | 0 | 1
1x0956 | Active alarm 456 | Alarm 31:6 Pressure regulation, extract air pressure sensor no. 6 communication error | 0 | 1
1x0957 | Active alarm 457 | Alarm 31:7 Pressure regulation, extract air pressure below set point alarm limit | 0 | 1
1x0958 | Active alarm 458 | Alarm 31:8 Pressure regulation, extract air pressure above set point alarm limit | 0 | 1
1x0959 | Active alarm 459 |  | 0 | 1
1x0960 | Active alarm 460 |  | 0 | 1
1x0961 | Active alarm 461 |  | 0 | 1
1x0962 | Active alarm 462 |  | 0 | 1
1x0963 | Active alarm 463 |  | 0 | 1
1x0964 | Active alarm 464 |  | 0 | 1
1x0965 | Active alarm 465 |  | 0 | 1
1x0966 | Active alarm 466 | Alarm 32:1 ReCO2, I/O-module no. 0 communication error | 0 | 1
1x0967 | Active alarm 467 | Alarm 32:2 ReCO2, pressure sensor no. 0 communication error | 0 | 1
1x0968 | Active alarm 468 | Alarm 32:3 ReCO2, recirculation damper monitoring tripped | 0 | 1
1x0969 | Active alarm 469 | Alarm 32:4 ReCO2, outdoor air damper monitoring tripped | 0 | 1
1x0970 | Active alarm 470 |  | 0 | 1
1x0971 | Active alarm 471 |  | 0 | 1
1x0972 | Active alarm 472 |  | 0 | 1
1x0973 | Active alarm 473 |  | 0 | 1
1x0974 | Active alarm 474 |  | 0 | 1
1x0975 | Active alarm 475 |  | 0 | 1
1x0976 | Active alarm 476 |  | 0 | 1
1x0977 | Active alarm 477 |  | 0 | 1
1x0978 | Active alarm 478 |  | 0 | 1
1x0979 | Active alarm 479 |  | 0 | 1
1x0980 | Active alarm 480 |  | 0 | 1
1x0981 | Active alarm 481 | Alarm 33:1 Service period above alarm limit | 0 | 1
1x0982 | Active alarm 482 |  | 0 | 1
1x0983 | Active alarm 483 |  | 0 | 1
1x0984 | Active alarm 484 |  | 0 | 1
1x0985 | Active alarm 485 |  | 0 | 1
1x0986 | Active alarm 486 |  | 0 | 1
1x0987 | Active alarm 487 |  | 0 | 1
1x0988 | Active alarm 488 |  | 0 | 1
1x0989 | Active alarm 489 |  | 0 | 1
1x0990 | Active alarm 490 |  | 0 | 1
1x0991 | Active alarm 491 |  | 0 | 1
1x0992 | Active alarm 492 |  | 0 | 1
1x0993 | Active alarm 493 |  | 0 | 1
1x0994 | Active alarm 494 |  | 0 | 1
1x0995 | Active alarm 495 | Alarm 33:15 Lock function tripped | 0 | 1
1x0996 | Active alarm 496 | Alarm 34:1 External control I/O-module no. 3 communication error | 0 | 1
1x0997 | Active alarm 497 | Alarm 34:2 External control I/O-module no. 6 communication error | 0 | 1
1x0998 | Active alarm 498 |  | 0 | 1
1x0999 | Active alarm 499 |  | 0 | 1
1x1000 | Active alarm 500 |  | 0 | 1
1x1001 | Active alarm 501 |  | 0 | 1
1x1002 | Active alarm 502 |  | 0 | 1
1x1003 | Active alarm 503 |  | 0 | 1
1x1004 | Active alarm 504 |  | 0 | 1
1x1005 | Active alarm 505 |  | 0 | 1
1x1006 | Active alarm 506 |  | 0 | 1
1x1007 | Active alarm 507 |  | 0 | 1
1x1008 | Active alarm 508 |  | 0 | 1
1x1009 | Active alarm 509 |  | 0 | 1
1x1010 | Active alarm 510 |  | 0 | 1
1x1011 | Active alarm 511 | Alarm 35:1 Booster diffusers, I/O-module no. 8 communication error | 0 | 1
1x1012 | Active alarm 512 |  | 0 | 1
1x1013 | Active alarm 513 |  | 0 | 1
1x1014 | Active alarm 514 |  | 0 | 1
1x1015 | Active alarm 515 |  | 0 | 1
1x1016 | Active alarm 516 |  | 0 | 1
1x1017 | Active alarm 517 |  | 0 | 1
1x1018 | Active alarm 518 |  | 0 | 1
1x1019 | Active alarm 519 |  | 0 | 1
1x1020 | Active alarm 520 |  | 0 | 1
1x1021 | Active alarm 521 |  | 0 | 1
1x1022 | Active alarm 522 |  | 0 | 1
1x1023 | Active alarm 523 |  | 0 | 1
1x1024 | Active alarm 524 |  | 0 | 1
1x1025 | Active alarm 525 |  | 0 | 1
1x1026 | Active alarm 526 | Alarm 36:1 External BMS control I/O-module no. A communication error | 0 | 1 |  |  | 1.20
1x1027 | Active alarm 527 | Alarm 36:2 External BMS control I/O-module no. A temperature sensor no. 1 defective | 0 | 1 |  |  | 1.20
1x1028 | Active alarm 528 | Alarm 36:3 External BMS control I/O-module no. A temperature sensor no. 2 defective | 0 | 1 |  |  | 1.20
1x1029 | Active alarm 529 |  | 0 | 1 |  |  | 1.20
1x1030 | Active alarm 530 |  | 0 | 1 |  |  | 1.20
1x1031 | Active alarm 531 | Alarm 36:6 External BMS control I/O-module no. B communication error | 0 | 1 |  |  | 1.20
1x1032 | Active alarm 532 | Alarm 36:7 External BMS control I/O-module no. B temperature sensor no. 1 defective | 0 | 1 |  |  | 1.20
1x1033 | Active alarm 533 | Alarm 36:8 External BMS control I/O-module no. B temperature sensor no. 2 defective | 0 | 1 |  |  | 1.20
1x1034 | Active alarm 534 |  | 0 | 1 |  |  | 1.20
1x1035 | Active alarm 535 |  | 0 | 1 |  |  | 1.20
1x1036 | Active alarm 536 | Alarm 36:11 External BMS control I/O-module no. C communication error | 0 | 1 |  |  | 1.20
1x1037 | Active alarm 537 | Alarm 36:12 External BMS control I/O-module no. C temperature sensor no. 1 defective | 0 | 1 |  |  | 1.20
1x1038 | Active alarm 538 | Alarm 36:13 External BMS control I/O-module no. C temperature sensor no. 2 defective | 0 | 1 |  |  | 1.20
1x1039 | Active alarm 539 |  | 0 | 1
1x1040 | Active alarm 540 |  | 0 | 1
1x1041 | Active alarm 541 | Alarm 37:1 Multilogic com. error | 0 | 1 |  |  | 2.48
1x1042 | Active alarm 542 |  | 0 | 1
1x1043 | Active alarm 543 |  | 0 | 1
1x1044 | Active alarm 544 |  | 0 | 1
1x1045 | Active alarm 545 |  | 0 | 1
1x1046 | Active alarm 546 |  | 0 | 1
1x1047 | Active alarm 547 |  | 0 | 1
1x1048 | Active alarm 548 |  | 0 | 1
1x1049 | Active alarm 549 |  | 0 | 1
1x1050 | Active alarm 550 |  | 0 | 1
1x1051 | Active alarm 551 |  | 0 | 1
1x1052 | Active alarm 552 |  | 0 | 1
1x1053 | Active alarm 553 |  | 0 | 1
1x1054 | Active alarm 554 |  | 0 | 1
1x1055 | Active alarm 555 |  | 0 | 1
1x1056 | Active alarm 556 | Alarm 38:1 MIRU Control no. 1 communication error | 0 | 1
1x1057 | Active alarm 557 | Alarm 38:2 MIRU Control no. 1 motor controller alarm tripped | 0 | 1
1x1058 | Active alarm 558 | Alarm 38:3 MIRU Control no. 1 motor controller communication error | 0 | 1
1x1059 | Active alarm 559 | Alarm 38:4 MIRU Control no. 1 air flow pressure sensor no. 0 communication error | 0 | 1
1x1060 | Active alarm 560 | Alarm 38:5 MIRU Control no. 1 pressure regulation sensor no. 1 communication error | 0 | 1
1x1061 | Active alarm 561 | Alarm 38:6 MIRU Control no. 1 temperature sensor defective | 0 | 1
1x1062 | Active alarm 562 | Alarm 38:7 MIRU Control no. 1 air flow/pressure set point deviation from alarm limit | 0 | 1
1x1063 | Active alarm 563 | Alarm 38:8 MIRU 1 air flow below set point alarm limit | 0 | 1 |  |  | 1.25
1x1064 | Active alarm 564 | Alarm 38:9 MIRU 1 air flow above set point alarm limit | 0 | 1 |  |  | 1.25
1x1065 | Active alarm 565 | Alarm 38:10 MIRU 1 pressure below set point alarm limit | 0 | 1 |  |  | 1.25
1x1066 | Active alarm 566 | Alarm 38:11 MIRU 1 pressure above set point alarm limit | 0 | 1 |  |  | 1.25
1x1067 | Active alarm 567 |  | 0 | 1
1x1068 | Active alarm 568 |  | 0 | 1
1x1069 | Active alarm 569 |  | 0 | 1
1x1070 | Active alarm 570 |  | 0 | 1
1x1071 | Active alarm 571 | Alarm 39:1 MIRU Control no. 2 communication error | 0 | 1
1x1072 | Active alarm 572 | Alarm 39:2 MIRU Control no. 2 motor controller alarm tripped | 0 | 1
1x1073 | Active alarm 573 | Alarm 39:3 MIRU Control no. 2 motor controller communication error | 0 | 1
1x1074 | Active alarm 574 | Alarm 39:4 MIRU Control no. 2 air flow pressure sensor no. 0 communication error | 0 | 1
1x1075 | Active alarm 575 | Alarm 39:5 MIRU Control no. 2 pressure regulation sensor no. 1 communication error | 0 | 1
1x1076 | Active alarm 576 | Alarm 39:6 MIRU Control no. 2 temperature sensor defective | 0 | 1
1x1077 | Active alarm 577 | Alarm 39:7 MIRU Control no. 2 air flow/pressure set point deviation from alarm limit | 0 | 1
1x1078 | Active alarm 578 | Alarm 39:8 MIRU 2 air flow below set point alarm limit | 0 | 1 |  |  | 1.25
1x1079 | Active alarm 579 | Alarm 39:9 MIRU 2 air flow above set point alarm limit | 0 | 1 |  |  | 1.25
1x1080 | Active alarm 580 | Alarm 39:10 MIRU 2 pressure below set point alarm limit | 0 | 1 |  |  | 1.25
1x1081 | Active alarm 581 | Alarm 39:11 MIRU 2 pressure above set point alarm limit | 0 | 1 |  |  | 1.25
1x1082 | Active alarm 582 |  | 0 | 1
1x1083 | Active alarm 583 |  | 0 | 1
1x1084 | Active alarm 584 |  | 0 | 1
1x1085 | Active alarm 585 |  | 0 | 1
1x1086 | Active alarm 586 | Alarm 40:1 MIRU Control no. 3 communication error | 0 | 1
1x1087 | Active alarm 587 | Alarm 40:2 MIRU Control no. 3 motor controller alarm tripped | 0 | 1
1x1088 | Active alarm 588 | Alarm 40:3 MIRU Control no. 3 motor controller communication error | 0 | 1
1x1089 | Active alarm 589 | Alarm 40:4 MIRU Control no. 3 air flow pressure sensor no. 0 communication error | 0 | 1
1x1090 | Active alarm 590 | Alarm 40:5 MIRU Control no. 3 pressure regulation sensor no. 1 communication error | 0 | 1
1x1091 | Active alarm 591 | Alarm 40:6 MIRU Control no. 3 temperature sensor defective | 0 | 1
1x1092 | Active alarm 592 | Alarm 40:7 MIRU Control no. 3 air flow/pressure set point deviation from alarm limit | 0 | 1
1x1093 | Active alarm 593 | Alarm 40:8 MIRU 3 air flow below set point alarm limit | 0 | 1 |  |  | 1.25
1x1094 | Active alarm 594 | Alarm 40:9 MIRU 3 air flow above set point alarm limit | 0 | 1 |  |  | 1.25
1x1095 | Active alarm 595 | Alarm 40:10 MIRU 3 pressure below set point alarm limit | 0 | 1 |  |  | 1.25
1x1096 | Active alarm 596 | Alarm 40:11 MIRU 3 pressure above set point alarm limit | 0 | 1 |  |  | 1.25
1x1097 | Active alarm 597 |  | 0 | 1
1x1098 | Active alarm 598 |  | 0 | 1
1x1099 | Active alarm 599 |  | 0 | 1
1x1100 | Active alarm 600 |  | 0 | 1
1x1101 | Active alarm 601 | Alarm 41:1 MIRU Control no. 4 communication error | 0 | 1
1x1102 | Active alarm 602 | Alarm 41:2 MIRU Control no. 4 motor controller alarm tripped | 0 | 1
1x1103 | Active alarm 603 | Alarm 41:3 MIRU Control no. 4 motor controller communication error | 0 | 1
1x1104 | Active alarm 604 | Alarm 41:4 MIRU Control no. 4 air flow pressure sensor no. 0 communication error | 0 | 1
1x1105 | Active alarm 605 | Alarm 41:5 MIRU Control no. 4 pressure regulation sensor no. 1 communication error | 0 | 1
1x1106 | Active alarm 606 | Alarm 41:6 MIRU Control no. 4 temperature sensor defective | 0 | 1
1x1107 | Active alarm 607 | Alarm 41:7 MIRU Control no. 4 air flow/pressure set point deviation from alarm limit | 0 | 1
1x1108 | Active alarm 608 |  | 0 | 1
1x1109 | Active alarm 609 |  | 0 | 1
1x1110 | Active alarm 610 |  | 0 | 1
1x1111 | Active alarm 611 |  | 0 | 1
1x1112 | Active alarm 612 |  | 0 | 1
1x1113 | Active alarm 613 |  | 0 | 1
1x1114 | Active alarm 614 |  | 0 | 1
1x1115 | Active alarm 615 |  | 0 | 1
1x1116 | Active alarm 616 | Alarm 42:1 MIRU Control no. 5 communication error | 0 | 1
1x1117 | Active alarm 617 | Alarm 42:2 MIRU Control no. 5 motor controller alarm tripped | 0 | 1
1x1118 | Active alarm 618 | Alarm 42:3 MIRU Control no. 5 motor controller communication error | 0 | 1
1x1119 | Active alarm 619 | Alarm 42:4 MIRU Control no. 5 air flow pressure sensor no. 0 communication error | 0 | 1
1x1120 | Active alarm 620 | Alarm 42:5 MIRU Control no. 5 pressure regulation sensor no. 1 communication error | 0 | 1
1x1121 | Active alarm 621 | Alarm 42:6 MIRU Control no. 5 temperature sensor defective | 0 | 1
1x1122 | Active alarm 622 | Alarm 42:7 MIRU Control no. 5 air flow/pressure set point deviation from alarm limit | 0 | 1
1x1123 | Active alarm 623 |  | 0 | 1
1x1124 | Active alarm 624 |  | 0 | 1
1x1125 | Active alarm 625 |  | 0 | 1
1x1126 | Active alarm 626 |  | 0 | 1
1x1127 | Active alarm 627 |  | 0 | 1
1x1128 | Active alarm 628 |  | 0 | 1
1x1129 | Active alarm 629 |  | 0 | 1
1x1130 | Active alarm 630 |  | 0 | 1
1x1131 | Active alarm 631 | Alarm 43:1 MIRU Control no. 6 communication error | 0 | 1
1x1132 | Active alarm 632 | Alarm 43:2 MIRU Control no. 6 motor controller alarm tripped | 0 | 1
1x1133 | Active alarm 633 | Alarm 43:3 MIRU Control no. 6 motor controller communication error | 0 | 1
1x1134 | Active alarm 634 | Alarm 43:4 MIRU Control no. 6 air flow pressure sensor no. 0 communication error | 0 | 1
1x1135 | Active alarm 635 | Alarm 43:5 MIRU Control no. 6 pressure regulation sensor no. 1 communication error | 0 | 1
1x1136 | Active alarm 636 | Alarm 43:6 MIRU Control no. 6 temperature sensor defective | 0 | 1
1x1137 | Active alarm 637 | Alarm 43:7 MIRU Control no. 6 air flow/pressure set point deviation from alarm limit | 0 | 1
1x1138 | Active alarm 638 |  | 0 | 1
1x1139 | Active alarm 639 |  | 0 | 1
1x1140 | Active alarm 640 |  | 0 | 1
1x1141 | Active alarm 641 |  | 0 | 1
1x1142 | Active alarm 642 |  | 0 | 1
1x1143 | Active alarm 643 |  | 0 | 1
1x1144 | Active alarm 644 |  | 0 | 1
1x1145 | Active alarm 645 |  | 0 | 1
1x1146 | Active alarm 646 | Alarm 44:1 MIRU Control no. 7 communication error | 0 | 1
1x1147 | Active alarm 647 | Alarm 44:2 MIRU Control no. 7 motor controller alarm tripped | 0 | 1
1x1148 | Active alarm 648 | Alarm 44:3 MIRU Control no. 7 motor controller communication error | 0 | 1
1x1149 | Active alarm 649 | Alarm 44:4 MIRU Control no. 7 air flow pressure sensor no. 0 communication error | 0 | 1
1x1150 | Active alarm 650 | Alarm 44:5 MIRU Control no. 7 pressure regulation sensor no. 1 communication error | 0 | 1
1x1151 | Active alarm 651 | Alarm 44:6 MIRU Control no. 7 temperature sensor defective | 0 | 1
1x1152 | Active alarm 652 | Alarm 44:7 MIRU Control no. 7 air flow/pressure set point deviation from alarm limit | 0 | 1
1x1153 | Active alarm 653 |  | 0 | 1
1x1154 | Active alarm 654 |  | 0 | 1
1x1155 | Active alarm 655 |  | 0 | 1
1x1156 | Active alarm 656 |  | 0 | 1
1x1157 | Active alarm 657 |  | 0 | 1
1x1158 | Active alarm 658 |  | 0 | 1
1x1159 | Active alarm 659 |  | 0 | 1
1x1160 | Active alarm 660 |  | 0 | 1
1x1161 | Active alarm 661 | Alarm 45:1 MIRU Control no. 8 communication error | 0 | 1
1x1162 | Active alarm 662 | Alarm 45:2 MIRU Control no. 8 motor controller alarm tripped | 0 | 1
1x1163 | Active alarm 663 | Alarm 45:3 MIRU Control no. 8 motor controller communication error | 0 | 1
1x1164 | Active alarm 664 | Alarm 45:4 MIRU Control no. 8 air flow pressure sensor no. 0 communication error | 0 | 1
1x1165 | Active alarm 665 | Alarm 45:5 MIRU Control no. 8 pressure regulation sensor no. 1 communication error | 0 | 1
1x1166 | Active alarm 666 | Alarm 45:6 MIRU Control no. 8 temperature sensor defective | 0 | 1
1x1167 | Active alarm 667 | Alarm 45:7 MIRU Control no. 8 air flow/pressure set point deviation from alarm limit | 0 | 1
1x1168 | Active alarm 668 |  | 0 | 1
1x1169 | Active alarm 669 |  | 0 | 1
1x1170 | Active alarm 670 |  | 0 | 1
1x1171 | Active alarm 671 |  | 0 | 1
1x1172 | Active alarm 672 |  | 0 | 1
1x1173 | Active alarm 673 |  | 0 | 1
1x1174 | Active alarm 674 |  | 0 | 1
1x1175 | Active alarm 675 |  | 0 | 1
1x1176 | Active alarm 676 | Alarm 46:1 MIRU Control no. 9 communication error | 0 | 1
1x1177 | Active alarm 677 | Alarm 46:2 MIRU Control no. 9 motor controller alarm tripped | 0 | 1
1x1178 | Active alarm 678 | Alarm 46:3 MIRU Control no. 9 motor controller communication error | 0 | 1
1x1179 | Active alarm 679 | Alarm 46:4 MIRU Control no. 9 air flow pressure sensor no. 0 communication error | 0 | 1
1x1180 | Active alarm 680 | Alarm 46:5 MIRU Control no. 9 pressure regulation sensor no. 1 communication error | 0 | 1
1x1181 | Active alarm 681 | Alarm 46:6 MIRU Control no. 9 temperature sensor defective | 0 | 1
1x1182 | Active alarm 682 | Alarm 46:7 MIRU Control no. 9 air flow/pressure set point deviation from alarm limit | 0 | 1
1x1183 | Active alarm 683 |  | 0 | 1
1x1184 | Active alarm 684 |  | 0 | 1
1x1185 | Active alarm 685 |  | 0 | 1
1x1186 | Active alarm 686 |  | 0 | 1
1x1187 | Active alarm 687 |  | 0 | 1
1x1188 | Active alarm 688 |  | 0 | 1
1x1189 | Active alarm 689 |  | 0 | 1
1x1190 | Active alarm 690 |  | 0 | 1
1x1191 | Active alarm 691 | Alarm 47:1 MIRU Control no. 10 communication error | 0 | 1
1x1192 | Active alarm 692 | Alarm 47:2 MIRU Control no. 10 motor controller alarm tripped | 0 | 1
1x1193 | Active alarm 693 | Alarm 47:3 MIRU Control no. 10 motor controller communication error | 0 | 1
1x1194 | Active alarm 694 | Alarm 47:4 MIRU Control no. 10 air flow pressure sensor no. 0 communication error | 0 | 1
1x1195 | Active alarm 695 | Alarm 47:5 MIRU Control no. 10 pressure regulation sensor no. 1 communication error | 0 | 1
1x1196 | Active alarm 696 | Alarm 47:6 MIRU Control no. 10 temperature sensor defective | 0 | 1
1x1197 | Active alarm 697 | Alarm 47:7 MIRU Control no. 10 air flow/pressure set point deviation from alarm limit | 0 | 1
1x1198 | Active alarm 698 |  | 0 | 1
1x1199 | Active alarm 699 |  | 0 | 1
1x1200 | Active alarm 700 |  | 0 | 1
1x1201 | Active alarm 701 |  | 0 | 1
1x1202 | Active alarm 702 |  | 0 | 1
1x1203 | Active alarm 703 |  | 0 | 1
1x1204 | Active alarm 704 |  | 0 | 1
1x1205 | Active alarm 705 |  | 0 | 1
1x1206 | Active alarm 706 |  | 0 | 1
1x1207 | Active alarm 707 |  | 0 | 1
1x1208 | Active alarm 708 |  | 0 | 1
1x1209 | Active alarm 709 |  | 0 | 1
1x1210 | Active alarm 710 |  | 0 | 1
1x1211 | Active alarm 711 |  | 0 | 1
1x1212 | Active alarm 712 |  | 0 | 1
1x1213 | Active alarm 713 |  | 0 | 1
1x1214 | Active alarm 714 |  | 0 | 1
1x1215 | Active alarm 715 |  | 0 | 1
1x1216 | Active alarm 716 |  | 0 | 1
1x1217 | Active alarm 717 |  | 0 | 1
1x1218 | Active alarm 718 |  | 0 | 1
1x1219 | Active alarm 719 |  | 0 | 1
1x1220 | Active alarm 720 |  | 0 | 1
1x1221 | Active alarm 721 | Alarm 49:1 Supply air fan no. 1A communication error | 0 | 1
1x1222 | Active alarm 722 | Alarm 49:2 Supply air fan no. 1A motor controller over current | 0 | 1
1x1223 | Active alarm 723 | Alarm 49:3 Supply air fan no. 1A motor controller under voltage | 0 | 1
1x1224 | Active alarm 724 | Alarm 49:4 Supply air fan no. 1A motor controller over voltage | 0 | 1
1x1225 | Active alarm 725 | Alarm 49:5 Supply air fan no. 1A motor controller over temperature | 0 | 1
1x1226 | Active alarm 726 | Alarm 49:6 Supply air fan no. 1A motor controller start error | 0 | 1
1x1227 | Active alarm 727 | Alarm 49:7 Supply air fan no. 1A motor controller ripple error | 0 | 1
1x1228 | Active alarm 728 | Alarm 49:8 Supply air fan no. 1A motor controller phase error | 0 | 1
1x1229 | Active alarm 729 | Alarm 49:9 Supply air fan no. 1A motor controller internal memory error | 0 | 1
1x1230 | Active alarm 730 | Alarm 49:10 Supply air fan no. 1A motor controller current reduction | 0 | 1
1x1231 | Active alarm 731 | Alarm 49:11 Supply air fan no. 1A motor controller internal com. error | 0 | 1 |  |  | 1.18
1x1232 | Active alarm 732 |  | 0 | 1
1x1233 | Active alarm 733 |  | 0 | 1
1x1234 | Active alarm 734 |  | 0 | 1
1x1235 | Active alarm 735 |  | 0 | 1
1x1236 | Active alarm 736 | Alarm 50:1 Supply air fan no. 2A communication error | 0 | 1
1x1237 | Active alarm 737 | Alarm 50:2 Supply air fan no. 2A motor controller over current | 0 | 1
1x1238 | Active alarm 738 | Alarm 50:3 Supply air fan no. 2A motor controller under voltage | 0 | 1
1x1239 | Active alarm 739 | Alarm 50:4 Supply air fan no. 2A motor controller over voltage | 0 | 1
1x1240 | Active alarm 740 | Alarm 50:5 Supply air fan no. 2A motor controller over temperature | 0 | 1
1x1241 | Active alarm 741 | Alarm 50:6 Supply air fan no. 2A motor controller start error | 0 | 1
1x1242 | Active alarm 742 | Alarm 50:7 Supply air fan no. 2A motor controller ripple error | 0 | 1
1x1243 | Active alarm 743 | Alarm 50:8 Supply air fan no. 2A motor controller phase error | 0 | 1
1x1244 | Active alarm 744 | Alarm 50:9 Supply air fan no. 2A motor controller internal memory error | 0 | 1
1x1245 | Active alarm 745 | Alarm 50:10 Supply air fan no. 2A motor controller current reduction | 0 | 1
1x1246 | Active alarm 746 | Alarm 50:11 Supply air fan no. 2A motor controller internal com. Error | 0 | 1 |  |  | 1.18
1x1247 | Active alarm 747 |  | 0 | 1
1x1248 | Active alarm 748 |  | 0 | 1
1x1249 | Active alarm 749 |  | 0 | 1
1x1250 | Active alarm 750 |  | 0 | 1
1x1251 | Active alarm 751 | Alarm 51:1 Supply air fan no. 3A communication error | 0 | 1
1x1252 | Active alarm 752 | Alarm 51:2 Supply air fan no. 3A motor controller over current | 0 | 1
1x1253 | Active alarm 753 | Alarm 51:3 Supply air fan no. 3A motor controller under voltage | 0 | 1
1x1254 | Active alarm 754 | Alarm 51:4 Supply air fan no. 3A motor controller over voltage | 0 | 1
1x1255 | Active alarm 755 | Alarm 51:5 Supply air fan no. 3A motor controller over temperature | 0 | 1
1x1256 | Active alarm 756 | Alarm 51:6 Supply air fan no. 3A motor controller start error | 0 | 1
1x1257 | Active alarm 757 | Alarm 51:7 Supply air fan no. 3A motor controller ripple error | 0 | 1
1x1258 | Active alarm 758 | Alarm 51:8 Supply air fan no. 3A motor controller phase error | 0 | 1
1x1259 | Active alarm 759 | Alarm 51:9 Supply air fan no. 3A motor controller internal memory error | 0 | 1
1x1260 | Active alarm 760 | Alarm 51:10 Supply air fan no. 3A motor controller current reduction | 0 | 1
1x1261 | Active alarm 761 | Alarm 51:11 Supply air fan no. 3A motor controller internal com. error | 0 | 1 |  |  | 1.18
1x1262 | Active alarm 762 |  | 0 | 1
1x1263 | Active alarm 763 |  | 0 | 1
1x1264 | Active alarm 764 |  | 0 | 1
1x1265 | Active alarm 765 |  | 0 | 1
1x1266 | Active alarm 766 | Alarm 52:1 Supply air fan no. 1B communication error | 0 | 1
1x1267 | Active alarm 767 | Alarm 52:2 Supply air fan no. 1B motor controller over current | 0 | 1
1x1268 | Active alarm 768 | Alarm 52:3 Supply air fan no. 1B motor controller under voltage | 0 | 1
1x1269 | Active alarm 769 | Alarm 52:4 Supply air fan no. 1B motor controller over voltage | 0 | 1
1x1270 | Active alarm 770 | Alarm 52:5 Supply air fan no. 1B motor controller over temperature | 0 | 1
1x1271 | Active alarm 771 | Alarm 52:6 Supply air fan no. 1B motor controller start error | 0 | 1
1x1272 | Active alarm 772 | Alarm 52:7 Supply air fan no. 1B motor controller ripple error | 0 | 1
1x1273 | Active alarm 773 | Alarm 52:8 Supply air fan no. 1B motor controller phase error | 0 | 1
1x1274 | Active alarm 774 | Alarm 52:9 Supply air fan no. 1B motor controller internal memory error | 0 | 1
1x1275 | Active alarm 775 | Alarm 52:10 Supply air fan no. 1B motor controller current reduction | 0 | 1
1x1276 | Active alarm 776 |  | 0 | 1
1x1277 | Active alarm 777 |  | 0 | 1
1x1278 | Active alarm 778 |  | 0 | 1
1x1279 | Active alarm 779 |  | 0 | 1
1x1280 | Active alarm 780 |  | 0 | 1
1x1281 | Active alarm 781 | Alarm 53:1 Supply air fan no. 2B communication error | 0 | 1
1x1282 | Active alarm 782 | Alarm 53:2 Supply air fan no. 2B motor controller over current | 0 | 1
1x1283 | Active alarm 783 | Alarm 53:3 Supply air fan no. 2B motor controller under voltage | 0 | 1
1x1284 | Active alarm 784 | Alarm 53:4 Supply air fan no. 2B motor controller over voltage | 0 | 1
1x1285 | Active alarm 785 | Alarm 53:5 Supply air fan no. 2B motor controller over temperature | 0 | 1
1x1286 | Active alarm 786 | Alarm 53:6 Supply air fan no. 2B motor controller start error | 0 | 1
1x1287 | Active alarm 787 | Alarm 53:7 Supply air fan no. 2B motor controller ripple error | 0 | 1
1x1288 | Active alarm 788 | Alarm 53:8 Supply air fan no. 2B motor controller phase error | 0 | 1
1x1289 | Active alarm 789 | Alarm 53:9 Supply air fan no. 2B motor controller internal memory error | 0 | 1
1x1290 | Active alarm 790 | Alarm 53:10 Supply air fan no. 2B motor controller current reduction | 0 | 1
1x1291 | Active alarm 791 |  | 0 | 1
1x1292 | Active alarm 792 |  | 0 | 1
1x1293 | Active alarm 793 |  | 0 | 1
1x1294 | Active alarm 794 |  | 0 | 1
1x1295 | Active alarm 795 |  | 0 | 1
1x1296 | Active alarm 796 | Alarm 54:1 Supply air fan no. 3B communication error | 0 | 1
1x1297 | Active alarm 797 | Alarm 54:2 Supply air fan no. 3B motor controller over current | 0 | 1
1x1298 | Active alarm 798 | Alarm 54:3 Supply air fan no. 3B motor controller under voltage | 0 | 1
1x1299 | Active alarm 799 | Alarm 54:4 Supply air fan no. 3B motor controller over voltage | 0 | 1
1x1300 | Active alarm 800 | Alarm 54:5 Supply air fan no. 3B motor controller over temperature | 0 | 1
1x1301 | Active alarm 801 | Alarm 54:6 Supply air fan no. 3B motor controller start error | 0 | 1
1x1302 | Active alarm 802 | Alarm 54:7 Supply air fan no. 3B motor controller ripple error | 0 | 1
1x1303 | Active alarm 803 | Alarm 54:8 Supply air fan no. 3B motor controller phase error | 0 | 1
1x1304 | Active alarm 804 | Alarm 54:9 Supply air fan no. 3B motor controller internal memory error | 0 | 1
1x1305 | Active alarm 805 | Alarm 54:10 Supply air fan no. 3B motor controller current reduction | 0 | 1
1x1306 | Active alarm 806 |  | 0 | 1
1x1307 | Active alarm 807 |  | 0 | 1
1x1308 | Active alarm 808 |  | 0 | 1
1x1309 | Active alarm 809 |  | 0 | 1
1x1310 | Active alarm 810 |  | 0 | 1
1x1311 | Active alarm 811 | Alarm 55:1 Extract air fan no. 1A communication error | 0 | 1
1x1312 | Active alarm 812 | Alarm 55:2 Extract air fan no. 1A motor controller over current | 0 | 1
1x1313 | Active alarm 813 | Alarm 55:3 Extract air fan no. 1A motor controller under voltage | 0 | 1
1x1314 | Active alarm 814 | Alarm 55:4 Extract air fan no. 1A motor controller over voltage | 0 | 1
1x1315 | Active alarm 815 | Alarm 55:5 Extract air fan no. 1A motor controller over temperature | 0 | 1
1x1316 | Active alarm 816 | Alarm 55:6 Extract air fan no. 1A motor controller start error | 0 | 1
1x1317 | Active alarm 817 | Alarm 55:7 Extract air fan no. 1A motor controller ripple error | 0 | 1
1x1318 | Active alarm 818 | Alarm 55:8 Extract air fan no. 1A motor controller phase error | 0 | 1
1x1319 | Active alarm 819 | Alarm 55:9 Extract air fan no. 1A motor controller internal memory error | 0 | 1
1x1320 | Active alarm 820 | Alarm 55:10 Extract air fan no. 1A motor controller current reduction | 0 | 1
1x1321 | Active alarm 821 | Alarm 55:11 Extract air fan no. 1A motor controller internal com. error | 0 | 1 |  |  | 1.18
1x1322 | Active alarm 822 |  | 0 | 1
1x1323 | Active alarm 823 |  | 0 | 1
1x1324 | Active alarm 824 |  | 0 | 1
1x1325 | Active alarm 825 |  | 0 | 1
1x1326 | Active alarm 826 | Alarm 56:1 Extract air fan no. 2A communication error | 0 | 1
1x1327 | Active alarm 827 | Alarm 56:2 Extract air fan no. 2A motor controller over current | 0 | 1
1x1328 | Active alarm 828 | Alarm 56:3 Extract air fan no. 2A motor controller under voltage | 0 | 1
1x1329 | Active alarm 829 | Alarm 56:4 Extract air fan no. 2A motor controller over voltage | 0 | 1
1x1330 | Active alarm 830 | Alarm 56:5 Extract air fan no. 2A motor controller over temperature | 0 | 1
1x1331 | Active alarm 831 | Alarm 56:6 Extract air fan no. 2A motor controller start error | 0 | 1
1x1332 | Active alarm 832 | Alarm 56:7 Extract air fan no. 2A motor controller ripple error | 0 | 1
1x1333 | Active alarm 833 | Alarm 56:8 Extract air fan no. 2A motor controller phase error | 0 | 1
1x1334 | Active alarm 834 | Alarm 56:9 Extract air fan no. 2A motor controller internal memory error | 0 | 1
1x1335 | Active alarm 835 | Alarm 56:10 Extract air fan no. 2A motor controller current reduction | 0 | 1
1x1336 | Active alarm 836 | Alarm 56:11 Extract air fan no. 2A motor controller internal com. Error | 0 | 1 |  |  | 1.18
1x1337 | Active alarm 837 |  | 0 | 1
1x1338 | Active alarm 838 |  | 0 | 1
1x1339 | Active alarm 839 |  | 0 | 1
1x1340 | Active alarm 840 |  | 0 | 1
1x1341 | Active alarm 841 | Alarm 57:1 Extract air fan no. 3A communication error | 0 | 1
1x1342 | Active alarm 842 | Alarm 57:2 Extract air fan no. 3A motor controller over current | 0 | 1
1x1343 | Active alarm 843 | Alarm 57:3 Extract air fan no. 3A motor controller under voltage | 0 | 1
1x1344 | Active alarm 844 | Alarm 57:4 Extract air fan no. 3A motor controller over voltage | 0 | 1
1x1345 | Active alarm 845 | Alarm 57:5 Extract air fan no. 3A motor controller over temperature | 0 | 1
1x1346 | Active alarm 846 | Alarm 57:6 Extract air fan no. 3A motor controller start error | 0 | 1
1x1347 | Active alarm 847 | Alarm 57:7 Extract air fan no. 3A motor controller ripple error | 0 | 1
1x1348 | Active alarm 848 | Alarm 57:8 Extract air fan no. 3A motor controller phase error | 0 | 1
1x1349 | Active alarm 849 | Alarm 57:9 Extract air fan no. 3A motor controller internal memory error | 0 | 1
1x1350 | Active alarm 850 | Alarm 57:10 Extract air fan no. 3A motor controller current reduction | 0 | 1
1x1351 | Active alarm 851 | Alarm 57:11 Extract air fan no. 3A motor controller internal com. error | 0 | 1 |  |  | 1.18
1x1352 | Active alarm 852 |  | 0 | 1
1x1353 | Active alarm 853 |  | 0 | 1
1x1354 | Active alarm 854 |  | 0 | 1
1x1355 | Active alarm 855 |  | 0 | 1
1x1356 | Active alarm 856 | Alarm 58:1 Extract air fan no. 1B communication error | 0 | 1
1x1357 | Active alarm 857 | Alarm 58:2 Extract air fan no. 1B motor controller over current | 0 | 1
1x1358 | Active alarm 858 | Alarm 58:3 Extract air fan no. 1B motor controller under voltage | 0 | 1
1x1359 | Active alarm 859 | Alarm 58:4 Extract air fan no. 1B motor controller over voltage | 0 | 1
1x1360 | Active alarm 860 | Alarm 58:5 Extract air fan no. 1B motor controller over temperature | 0 | 1
1x1361 | Active alarm 861 | Alarm 58:6 Extract air fan no. 1B motor controller start error | 0 | 1
1x1362 | Active alarm 862 | Alarm 58:7 Extract air fan no. 1B motor controller ripple error | 0 | 1
1x1363 | Active alarm 863 | Alarm 58:8 Extract air fan no. 1B motor controller phase error | 0 | 1
1x1364 | Active alarm 864 | Alarm 58:9 Extract air fan no. 1B motor controller internal memory error | 0 | 1
1x1365 | Active alarm 865 | Alarm 58:10 Extract air fan no. 1B motor controller current reduction | 0 | 1
1x1366 | Active alarm 866 |  | 0 | 1
1x1367 | Active alarm 867 |  | 0 | 1
1x1368 | Active alarm 868 |  | 0 | 1
1x1369 | Active alarm 869 |  | 0 | 1
1x1370 | Active alarm 870 |  | 0 | 1
1x1371 | Active alarm 871 | Alarm 59:1 Extract air fan no. 2B communication error | 0 | 1
1x1372 | Active alarm 872 | Alarm 59:2 Extract air fan no. 2B motor controller over current | 0 | 1
1x1373 | Active alarm 873 | Alarm 59:3 Extract air fan no. 2B motor controller under voltage | 0 | 1
1x1374 | Active alarm 874 | Alarm 59:4 Extract air fan no. 2B motor controller over voltage | 0 | 1
1x1375 | Active alarm 875 | Alarm 59:5 Extract air fan no. 2B motor controller over temperature | 0 | 1
1x1376 | Active alarm 876 | Alarm 59:6 Extract air fan no. 2B motor controller start error | 0 | 1
1x1377 | Active alarm 877 | Alarm 59:7 Extract air fan no. 2B motor controller ripple error | 0 | 1
1x1378 | Active alarm 878 | Alarm 59:8 Extract air fan no. 2B motor controller phase error | 0 | 1
1x1379 | Active alarm 879 | Alarm 59:9 Extract air fan no. 2B motor controller internal memory error | 0 | 1
1x1380 | Active alarm 880 | Alarm 59:10 Extract air fan no. 2B motor controller current reduction | 0 | 1
1x1381 | Active alarm 881 |  | 0 | 1
1x1382 | Active alarm 882 |  | 0 | 1
1x1383 | Active alarm 883 |  | 0 | 1
1x1384 | Active alarm 884 |  | 0 | 1
1x1385 | Active alarm 885 |  | 0 | 1
1x1386 | Active alarm 886 | Alarm 60:1 Extract air fan no. 3B communication error | 0 | 1
1x1387 | Active alarm 887 | Alarm 60:2 Extract air fan no. 3B motor controller over current | 0 | 1
1x1388 | Active alarm 888 | Alarm 60:3 Extract air fan no. 3B motor controller under voltage | 0 | 1
1x1389 | Active alarm 889 | Alarm 60:4 Extract air fan no. 3B motor controller over voltage | 0 | 1
1x1390 | Active alarm 890 | Alarm 60:5 Extract air fan no. 3B motor controller over temperature | 0 | 1
1x1391 | Active alarm 891 | Alarm 60:6 Extract air fan no. 3B motor controller start error | 0 | 1
1x1392 | Active alarm 892 | Alarm 60:7 Extract air fan no. 3B motor controller ripple error | 0 | 1
1x1393 | Active alarm 893 | Alarm 60:8 Extract air fan no. 3B motor controller phase error | 0 | 1
1x1394 | Active alarm 894 | Alarm 60:9 Extract air fan no. 3B motor controller internal memory error | 0 | 1
1x1395 | Active alarm 895 | Alarm 60:10 Extract air fan no. 3B motor controller current reduction | 0 | 1
1x1396 | Active alarm 896 |  | 0 | 1
1x1397 | Active alarm 897 |  | 0 | 1
1x1398 | Active alarm 898 |  | 0 | 1
1x1399 | Active alarm 899 |  | 0 | 1
1x1400 | Active alarm 900 |  | 0 | 1
1x1401 | Active alarm 901 | Alarm 61:1 Supply air fan no. 1A I/O-module com. error | 0 | 1 |  |  | 1.18
1x1402 | Active alarm 902 |  | 0 | 1
1x1403 | Active alarm 903 |  | 0 | 1
1x1404 | Active alarm 904 |  | 0 | 1
1x1405 | Active alarm 905 |  | 0 | 1
1x1406 | Active alarm 906 | Alarm 61:6 Supply air fan no. 2A I/O-module com. error | 0 | 1 |  |  | 1.18
1x1407 | Active alarm 907 |  | 0 | 1
1x1408 | Active alarm 908 |  | 0 | 1
1x1409 | Active alarm 909 |  | 0 | 1
1x1410 | Active alarm 910 |  | 0 | 1
1x1411 | Active alarm 911 | Alarm 61:11 Supply air fan no. 3A I/O-module com. error | 0 | 1 |  |  | 1.18
1x1412 | Active alarm 912 |  | 0 | 1
1x1413 | Active alarm 913 |  | 0 | 1
1x1414 | Active alarm 914 |  | 0 | 1
1x1415 | Active alarm 915 |  | 0 | 1
1x1416 | Active alarm 916 | Alarm 62:1 Extract air fan no. 1A I/O-module com. error | 0 | 1 |  |  | 1.18
1x1417 | Active alarm 917 |  | 0 | 1
1x1418 | Active alarm 918 |  | 0 | 1
1x1419 | Active alarm 919 |  | 0 | 1
1x1420 | Active alarm 920 |  | 0 | 1
1x1421 | Active alarm 921 | Alarm 62:6 Extract air fan no. 2A I/O-module com. error | 0 | 1 |  |  | 1.18
1x1422 | Active alarm 922 |  | 0 | 1
1x1423 | Active alarm 923 |  | 0 | 1
1x1424 | Active alarm 924 |  | 0 | 1
1x1425 | Active alarm 925 |  | 0 | 1
1x1426 | Active alarm 926 | Alarm 62:11 Extract air fan no. 3A I/O-module com. error | 0 | 1 |  |  | 1.18
1x1427 | Active alarm 927 |  | 0 | 1
1x1428 | Active alarm 928 |  | 0 | 1
1x1429 | Active alarm 929 |  | 0 | 1
1x1430 | Active alarm 930 |  | 0 | 1
1x1431 | Active alarm 931 | Alarm 63:1 MIRU 1 I/O-module com. error | 0 | 1 |  |  | 1.25
1x1432 | Active alarm 932 |  | 0 | 1
1x1433 | Active alarm 933 |  | 0 | 1
1x1434 | Active alarm 934 |  | 0 | 1
1x1435 | Active alarm 935 |  | 0 | 1
1x1436 | Active alarm 936 | Alarm 63:6 MIRU 2 I/O-module com. error | 0 | 1 |  |  | 1.25
1x1437 | Active alarm 937 |  | 0 | 1
1x1438 | Active alarm 938 |  | 0 | 1
1x1439 | Active alarm 939 |  | 0 | 1
1x1440 | Active alarm 940 |  | 0 | 1
1x1441 | Active alarm 941 | Alarm 63:11 MIRU 3 I/O-module com. error | 0 | 1 |  |  | 1.25
1x1442 | Active alarm 942 |  | 0 | 1
1x1443 | Active alarm 943 |  | 0 | 1
1x1444 | Active alarm 944 |  | 0 | 1
1x1445 | Active alarm 945 |  | 0 | 1
1x1446 | Active alarm 946 | Alarm 64:1 Supply air fan no. 1A common A-alarm | 0 | 1 |  |  | 2.38
1x1447 | Active alarm 947 |  | 0 | 1
1x1448 | Active alarm 948 | Alarm 64:3 Supply air fan no. 1A common B-alarm | 0 | 1 |  |  | 2.38
1x1449 | Active alarm 949 |  | 0 | 1
1x1450 | Active alarm 950 | Alarm 64:5 Supply air fan no. 1A common warning | 0 | 1 |  |  | 2.38
1x1451 | Active alarm 951 | Alarm 64:6 Supply air fan no. 2A common A-alarm | 0 | 1 |  |  | 2.38
1x1452 | Active alarm 952 |  | 0 | 1
1x1453 | Active alarm 953 | Alarm 64:8 Supply air fan no. 2A common B-alarm | 0 | 1 |  |  | 2.38
1x1454 | Active alarm 954 |  | 0 | 1
1x1455 | Active alarm 955 | Alarm 64:10 Supply air fan no. 2A common warning | 0 | 1 |  |  | 2.38
1x1456 | Active alarm 956 | Alarm 64:11 Supply air fan no. 3A common A-alarm | 0 | 1 |  |  | 2.38
1x1457 | Active alarm 957 |  | 0 | 1
1x1458 | Active alarm 958 | Alarm 64:13 Supply air fan no. 3A common B-alarm | 0 | 1 |  |  | 2.38
1x1459 | Active alarm 959 |  | 0 | 1
1x1460 | Active alarm 960 | Alarm 64:15 Supply air fan no. 3A common warning | 0 | 1 |  |  | 2.38
1x1461 | Active alarm 961 | Alarm 65:1 Extract air fan no. 1A common A-alarm | 0 | 1 |  |  | 2.38
1x1462 | Active alarm 962 |  | 0 | 1
1x1463 | Active alarm 963 | Alarm 65:3 Extract air fan no. 1A common B-alarm | 0 | 1 |  |  | 2.38
1x1464 | Active alarm 964 |  | 0 | 1
1x1465 | Active alarm 965 | Alarm 65:5 Extract air fan no. 1A common warning | 0 | 1 |  |  | 2.38
1x1466 | Active alarm 966 | Alarm 65:6 Extract air fan no. 2A common A-alarm | 0 | 1 |  |  | 2.38
1x1467 | Active alarm 967 |  | 0 | 1
1x1468 | Active alarm 968 | Alarm 65:8 Extract air fan no. 2A common B-alarm | 0 | 1 |  |  | 2.38
1x1469 | Active alarm 969 |  | 0 | 1
1x1470 | Active alarm 970 | Alarm 65:10 Extract air fan no. 2A common warning | 0 | 1 |  |  | 2.38
1x1471 | Active alarm 971 | Alarm 65:11 Extract air fan no. 3A common A-alarm | 0 | 1 |  |  | 2.38
1x1472 | Active alarm 972 |  | 0 | 1
1x1473 | Active alarm 973 | Alarm 65:13 Extract air fan no. 3A common B-alarm | 0 | 1 |  |  | 2.38
1x1474 | Active alarm 974 |  | 0 | 1
1x1475 | Active alarm 975 | Alarm 65:15 Extract air fan no. 3A common warning | 0 | 1 |  |  | 2.38
1x1476 | Active alarm 976 |  | 0 | 1
1x1477 | Active alarm 977 |  | 0 | 1
1x1478 | Active alarm 978 |  | 0 | 1
1x1479 | Active alarm 979 |  | 0 | 1
1x1480 | Active alarm 980 |  | 0 | 1
1x1481 | Active alarm 981 |  | 0 | 1
1x1482 | Active alarm 982 |  | 0 | 1
1x1483 | Active alarm 983 |  | 0 | 1
1x1484 | Active alarm 984 |  | 0 | 1
1x1485 | Active alarm 985 |  | 0 | 1
1x1486 | Active alarm 986 |  | 0 | 1
1x1487 | Active alarm 987 |  | 0 | 1
1x1488 | Active alarm 988 |  | 0 | 1
1x1489 | Active alarm 989 |  | 0 | 1
1x1490 | Active alarm 990 |  | 0 | 1
1x1491 | Active alarm 991 |  | 0 | 1
1x1492 | Active alarm 992 |  | 0 | 1
1x1493 | Active alarm 993 |  | 0 | 1
1x1494 | Active alarm 994 |  | 0 | 1
1x1495 | Active alarm 995 |  | 0 | 1
1x1496 | Active alarm 996 |  | 0 | 1
1x1497 | Active alarm 997 |  | 0 | 1
1x1498 | Active alarm 998 |  | 0 | 1
1x1499 | Active alarm 999 |  | 0 | 1
1x1500 | Active alarm 1000 |  | 0 | 1
1x1501 | Active alarm 1001 |  | 0 | 1
1x1502 | Active alarm 1002 |  | 0 | 1
1x1503 | Active alarm 1003 |  | 0 | 1
1x1504 | Active alarm 1004 |  | 0 | 1
1x1505 | Active alarm 1005 |  | 0 | 1
1x1506 | Active alarm 1006 |  | 0 | 1
1x1507 | Active alarm 1007 |  | 0 | 1
1x1508 | Active alarm 1008 |  | 0 | 1
1x1509 | Active alarm 1009 |  | 0 | 1
1x1510 | Active alarm 1010 |  | 0 | 1
1x1511 | Active alarm 1011 |  | 0 | 1
1x1512 | Active alarm 1012 |  | 0 | 1
1x1513 | Active alarm 1013 |  | 0 | 1
1x1514 | Active alarm 1014 |  | 0 | 1
1x1515 | Active alarm 1015 |  | 0 | 1
1x1516 | Active alarm 1016 |  | 0 | 1
1x1517 | Active alarm 1017 |  | 0 | 1
1x1518 | Active alarm 1018 |  | 0 | 1
1x1519 | Active alarm 1019 |  | 0 | 1
1x1520 | Active alarm 1020 |  | 0 | 1
1x1521 | Active alarm 1021 |  | 0 | 1
1x1522 | Active alarm 1022 |  | 0 | 1
1x1523 | Active alarm 1023 |  | 0 | 1
1x1524 | Active alarm 1024 |  | 0 | 1
1x1525 | Active alarm 1025 |  | 0 | 1
1x1526 | Active alarm 1026 |  | 0 | 1
1x1527 | Active alarm 1027 |  | 0 | 1
1x1528 | Active alarm 1028 |  | 0 | 1
1x1529 | Active alarm 1029 |  | 0 | 1
1x1530 | Active alarm 1030 |  | 0 | 1
1x1531 | Active alarm 1031 |  | 0 | 1
1x1532 | Active alarm 1032 |  | 0 | 1
1x1533 | Active alarm 1033 |  | 0 | 1
1x1534 | Active alarm 1034 |  | 0 | 1
1x1535 | Active alarm 1035 |  | 0 | 1
1x1536 | Active alarm 1036 | Alarm 70:1 H/C controls com. Error | 0 | 1 |  |  | 1.23
1x1537 | Active alarm 1037 | Alarm 70:2 H/C controls internal memory error | 0 | 1 |  |  | 1.23
1x1538 | Active alarm 1038 | Alarm 70:3 H/C controls clock circuit defective | 0 | 1 |  |  | 1.23
1x1539 | Active alarm 1039 |  | 0 | 1
1x1540 | Active alarm 1040 | Alarm 70:5 H/C defrost pressure sensor no. D com. Error | 0 | 1 |  |  | 1.23
1x1541 | Active alarm 1041 | Alarm 70:6 H/C defrost I/O-module no. 5 com. Error | 0 | 1 |  |  | 1.23
1x1542 | Active alarm 1042 | Alarm 70:7 H/C defrost recirculation damper monitoring tripped | 0 | 1 |  |  | 1.23
1x1543 | Active alarm 1043 | Alarm 70:8 H/C defrost electrical heater overheat protection tripped | 0 | 1 |  |  | 1.23
1x1544 | Active alarm 1044 | Alarm 70:9 H/C defrost time above alarm limit | 0 | 1 |  |  | 1.23
1x1545 | Active alarm 1045 |  | 0 | 1
1x1546 | Active alarm 1046 | Alarm 70:11 H/C defrost interval above alarm limit | 0 | 1 |  |  | 1.27
1x1547 | Active alarm 1047 | Alarm 70:12 H/C wrong phase sequence | 0 | 1 |  |  | 1.27
1x1548 | Active alarm 1048 |  | 0 | 1
1x1549 | Active alarm 1049 |  | 0 | 1
1x1550 | Active alarm 1050 |  | 0 | 1
1x1551 | Active alarm 1051 | Alarm 71:1 H/C compressor motor control com. Error | 0 | 1 |  |  | 1.23
1x1552 | Active alarm 1052 | Alarm 71:2 H/C compressor motor control start error | 0 | 1 |  |  | 1.23
1x1553 | Active alarm 1053 | Alarm 71:3 H/C compressor motor controller over or under voltage | 0 | 1 |  |  | 1.23
1x1554 | Active alarm 1054 | Alarm 71:4 H/C compressor out of operation range | 0 | 1 |  |  | 1.23
1x1555 | Active alarm 1055 |  | 0 | 1
1x1556 | Active alarm 1056 |  | 0 | 1
1x1557 | Active alarm 1057 |  | 0 | 1
1x1558 | Active alarm 1058 |  | 0 | 1
1x1559 | Active alarm 1059 | Alarm 71:9 H/C expansion valve controller com. Error | 0 | 1 |  |  | 1.23
1x1560 | Active alarm 1060 |  | 0 | 1
1x1561 | Active alarm 1061 |  | 0 | 1
1x1562 | Active alarm 1062 |  | 0 | 1
1x1563 | Active alarm 1063 |  | 0 | 1
1x1564 | Active alarm 1064 |  | 0 | 1
1x1565 | Active alarm 1065 |  | 0 | 1
1x1566 | Active alarm 1066 | Alarm 72:1 H/C high pressure switch tripped | 0 | 1 |  |  | 1.23
1x1567 | Active alarm 1067 | Alarm 72:2 H/C high pressure above alarm limit | 0 | 1 |  |  | 1.23
1x1568 | Active alarm 1068 | Alarm 72:3 H/C thermal switch compressor no. 1 tripped | 0 | 1 |  |  | 2.46
1x1569 | Active alarm 1069 | Alarm 72:4 H/C discharge temperature above alarm limit | 0 | 1 |  |  | 1.23
1x1570 | Active alarm 1070 | Alarm 72:5 H/C discharge temperature sensor defective | 0 | 1 |  |  | 1.23
1x1571 | Active alarm 1071 | Alarm 72:6 H/C high pressure sensor defective | 0 | 1 |  |  | 1.23
1x1572 | Active alarm 1072 | Alarm 72:7 H/C low pressure sensor defective | 0 | 1 |  |  | 1.23
1x1573 | Active alarm 1073 | Alarm 72:8 H/C suction temperature sensor defective | 0 | 1 |  |  | 1.23
1x1574 | Active alarm 1074 | Alarm 72:9 H/C pressure difference below alarm limit | 0 | 1 |  |  | 1.23
1x1575 | Active alarm 1075 | Alarm 72:10 H/C maintenance and compressor | 0 | 1 |  |  | 1.23
1x1576 | Active alarm 1076 | Alarm 72:11 H/C superheat temperature below alarm limit | 0 | 1 |  |  | 1.23
1x1577 | Active alarm 1077 | Alarm 72:12 H/C unloading of low pressure | 0 | 1 |  |  | 1.23
1x1578 | Active alarm 1078 | Alarm 72:13 H/C unloading of high pressure | 0 | 1 |  |  | 1.23
1x1579 | Active alarm 1079 | Alarm 72:14 H/C low pressure below alarm limit | 0 | 1 |  |  | 1.23
1x1580 | Active alarm 1080 | Alarm 72:15 H/C thermal switch compressor no. 2 tripped | 0 | 1 |  |  | 2.46
1x1581 | Active alarm 1081 |  | 0 | 1
1x1582 | Active alarm 1082 |  | 0 | 1
1x1583 | Active alarm 1083 |  | 0 | 1
1x1584 | Active alarm 1084 |  | 0 | 1
1x1585 | Active alarm 1085 |  | 0 | 1
1x1586 | Active alarm 1086 |  | 0 | 1
1x1587 | Active alarm 1087 |  | 0 | 1
1x1588 | Active alarm 1088 |  | 0 | 1
1x1589 | Active alarm 1089 |  | 0 | 1
1x1590 | Active alarm 1090 |  | 0 | 1
1x1591 | Active alarm 1091 |  | 0 | 1
1x1592 | Active alarm 1092 |  | 0 | 1
1x1593 | Active alarm 1093 |  | 0 | 1
1x1594 | Active alarm 1094 |  | 0 | 1
1x1595 | Active alarm 1095 |  | 0 | 1
1x1596 | Active alarm 1096 |  | 0 | 1
1x1597 | Active alarm 1097 |  | 0 | 1
1x1598 | Active alarm 1098 |  | 0 | 1
1x1599 | Active alarm 1099 |  | 0 | 1
1x1600 | Active alarm 1100 |  | 0 | 1
1x1601 | Active alarm 1101 |  | 0 | 1
1x1602 | Active alarm 1102 |  | 0 | 1
1x1603 | Active alarm 1103 |  | 0 | 1
1x1604 | Active alarm 1104 |  | 0 | 1
1x1605 | Active alarm 1105 |  | 0 | 1
1x1606 | Active alarm 1106 |  | 0 | 1
1x1607 | Active alarm 1107 |  | 0 | 1
1x1608 | Active alarm 1108 |  | 0 | 1
1x1609 | Active alarm 1109 |  | 0 | 1
1x1610 | Active alarm 1110 |  | 0 | 1
1x1611 | Active alarm 1111 |  | 0 | 1
1x1612 | Active alarm 1112 |  | 0 | 1
1x1613 | Active alarm 1113 |  | 0 | 1
1x1614 | Active alarm 1114 |  | 0 | 1
1x1615 | Active alarm 1115 |  | 0 | 1
1x1616 | Active alarm 1116 |  | 0 | 1
1x1617 | Active alarm 1117 |  | 0 | 1
1x1618 | Active alarm 1118 |  | 0 | 1
1x1619 | Active alarm 1119 |  | 0 | 1
1x1620 | Active alarm 1120 |  | 0 | 1
1x1621 | Active alarm 1121 |  | 0 | 1
1x1622 | Active alarm 1122 |  | 0 | 1
1x1623 | Active alarm 1123 |  | 0 | 1
1x1624 | Active alarm 1124 |  | 0 | 1
1x1625 | Active alarm 1125 |  | 0 | 1
1x1626 | Active alarm 1126 |  | 0 | 1
1x1627 | Active alarm 1127 |  | 0 | 1
1x1628 | Active alarm 1128 |  | 0 | 1
1x1629 | Active alarm 1129 |  | 0 | 1
1x1630 | Active alarm 1130 |  | 0 | 1
1x1631 | Active alarm 1131 |  | 0 | 1
1x1632 | Active alarm 1132 |  | 0 | 1
1x1633 | Active alarm 1133 |  | 0 | 1
1x1634 | Active alarm 1134 |  | 0 | 1
1x1635 | Active alarm 1135 |  | 0 | 1
1x1636 | Active alarm 1136 |  | 0 | 1
1x1637 | Active alarm 1137 |  | 0 | 1
1x1638 | Active alarm 1138 |  | 0 | 1
1x1639 | Active alarm 1139 |  | 0 | 1
1x1640 | Active alarm 1140 |  | 0 | 1
1x1641 | Active alarm 1141 |  | 0 | 1
1x1642 | Active alarm 1142 | Alarm 77:2 MIRU 1 motor controller over current | 0 | 1 |  |  | 1.25
1x1643 | Active alarm 1143 | Alarm 77:3 MIRU 1 motor controller under voltage | 0 | 1 |  |  | 1.25
1x1644 | Active alarm 1144 | Alarm 77:4 MIRU 1 motor controller over voltage | 0 | 1 |  |  | 1.25
1x1645 | Active alarm 1145 | Alarm 77:5 MIRU 1 motor controller over temperature | 0 | 1 |  |  | 1.25
1x1646 | Active alarm 1146 | Alarm 77:6 MIRU 1 motor controller start error | 0 | 1 |  |  | 1.25
1x1647 | Active alarm 1147 | Alarm 77:7 MIRU 1 motor controller ripple error | 0 | 1 |  |  | 1.25
1x1648 | Active alarm 1148 | Alarm 77:8 MIRU 1 motor controller phase error | 0 | 1 |  |  | 1.25
1x1649 | Active alarm 1149 | Alarm 77:9 MIRU 1 motor controller internal memory error | 0 | 1 |  |  | 1.25
1x1650 | Active alarm 1150 | Alarm 77:10 MIRU 1 motor controller current reduction | 0 | 1 |  |  | 1.25
1x1651 | Active alarm 1151 | Alarm 77:11 MIRU 1 motor controller internal com. error | 0 | 1 |  |  | 1.25
1x1652 | Active alarm 1152 |  | 0 | 1
1x1653 | Active alarm 1153 |  | 0 | 1
1x1654 | Active alarm 1154 |  | 0 | 1
1x1655 | Active alarm 1155 |  | 0 | 1
1x1656 | Active alarm 1156 |  | 0 | 1
1x1657 | Active alarm 1157 | Alarm 78:2 MIRU 2 motor controller over current | 0 | 1 |  |  | 1.25
1x1658 | Active alarm 1158 | Alarm 78:3 MIRU 2 motor controller under voltage | 0 | 1 |  |  | 1.25
1x1659 | Active alarm 1159 | Alarm 78:4 MIRU 2 motor controller over voltage | 0 | 1 |  |  | 1.25
1x1660 | Active alarm 1160 | Alarm 78:5 MIRU 2 motor controller over temperature | 0 | 1 |  |  | 1.25
1x1661 | Active alarm 1161 | Alarm 78:6 MIRU 2 motor controller start error | 0 | 1 |  |  | 1.25
1x1662 | Active alarm 1162 | Alarm 78:7 MIRU 2 motor controller ripple error | 0 | 1 |  |  | 1.25
1x1663 | Active alarm 1163 | Alarm 78:8 MIRU 2 motor controller phase error | 0 | 1 |  |  | 1.25
1x1664 | Active alarm 1164 | Alarm 78:9 MIRU 2 motor controller internal memory error | 0 | 1 |  |  | 1.25
1x1665 | Active alarm 1165 | Alarm 78:10 MIRU 2 motor controller current reduction | 0 | 1 |  |  | 1.25
1x1666 | Active alarm 1166 | Alarm 78:11 MIRU 2 motor controller internal com. error | 0 | 1 |  |  | 1.25
1x1667 | Active alarm 1167 |  | 0 | 1
1x1668 | Active alarm 1168 |  | 0 | 1
1x1669 | Active alarm 1169 |  | 0 | 1
1x1670 | Active alarm 1170 |  | 0 | 1
1x1671 | Active alarm 1171 |  | 0 | 1
1x1672 | Active alarm 1172 | Alarm 79:2 MIRU 3 motor controller over current | 0 | 1 |  |  | 1.25
1x1673 | Active alarm 1173 | Alarm 79:3 MIRU 3 motor controller under voltage | 0 | 1 |  |  | 1.25
1x1674 | Active alarm 1174 | Alarm 79:4 MIRU 3 motor controller over voltage | 0 | 1 |  |  | 1.25
1x1675 | Active alarm 1175 | Alarm 79:5 MIRU 3 motor controller over temperature | 0 | 1 |  |  | 1.25
1x1676 | Active alarm 1176 | Alarm 79:6 MIRU 3 motor controller start error | 0 | 1 |  |  | 1.25
1x1677 | Active alarm 1177 | Alarm 79:7 MIRU 3 motor controller ripple error | 0 | 1 |  |  | 1.25
1x1678 | Active alarm 1178 | Alarm 79:8 MIRU 3 motor controller phase error | 0 | 1 |  |  | 1.25
1x1679 | Active alarm 1179 | Alarm 79:9 MIRU 3 motor controller internal memory error | 0 | 1 |  |  | 1.25
1x1680 | Active alarm 1180 | Alarm 79:10 MIRU 3 motor controller current reduction | 0 | 1 |  |  | 1.25
1x1681 | Active alarm 1181 | Alarm 79:11 MIRU 3 motor controller internal com. error | 0 | 1 |  |  | 1.25
1x1682 | Active alarm 1182 |  | 0 | 1
1x1683 | Active alarm 1183 |  | 0 | 1
1x1684 | Active alarm 1184 |  | 0 | 1
1x1685 | Active alarm 1185 |  | 0 | 1
1x1686 | Active alarm 1186 |  | 0 | 1
1x1687 | Active alarm 1187 |  | 0 | 1
1x1688 | Active alarm 1188 |  | 0 | 1
1x1689 | Active alarm 1189 |  | 0 | 1
1x1690 | Active alarm 1190 |  | 0 | 1
1x1691 | Active alarm 1191 |  | 0 | 1
1x1692 | Active alarm 1192 |  | 0 | 1
1x1693 | Active alarm 1193 |  | 0 | 1
1x1694 | Active alarm 1194 |  | 0 | 1
1x1695 | Active alarm 1195 |  | 0 | 1
1x1696 | Active alarm 1196 |  | 0 | 1
1x1697 | Active alarm 1197 |  | 0 | 1
1x1698 | Active alarm 1198 |  | 0 | 1
1x1699 | Active alarm 1199 |  | 0 | 1
1x1700 | Active alarm 1200 |  | 0 | 1
1x1701 | Active alarm 1201 |  | 0 | 1
1x1702 | Active alarm 1202 | Alarm 81:2 SMART Link no. 1 supply air flow below defrost alarm limit | 0 | 1 |  |  | 1.25
1x1703 | Active alarm 1203 | Alarm 81:3 SMART Link no. 1 High pressure switch tripped | 0 | 1 |  |  | 1.27
1x1704 | Active alarm 1204 | Alarm 81:4 SMART Link no. 1 High pressure above alarm limit | 0 | 1 |  |  | 1.27
1x1705 | Active alarm 1205 | Alarm 81:5 SMART Link no. 1 Low pressure below alarm limit | 0 | 1 |  |  | 1.27
1x1706 | Active alarm 1206 | Alarm 81:6 SMART Link no. 1 Evaporation temperature below alarm limit | 0 | 1 |  |  | 1.27
1x1707 | Active alarm 1207 | Alarm 81:7 SMART Link no. 1 Inverter group alarm (Power+) | 0 | 1 |  |  | 1.27
1x1708 | Active alarm 1208 | Alarm 81:8 SMART Link no. 1 Envelope alarm | 0 | 1 |  |  | 1.27
1x1709 | Active alarm 1209 | Alarm 81:9 SMART Link no. 1 Starting up of faulty compressor | 0 | 1 |  |  | 1.27
1x1710 | Active alarm 1210 | Alarm 81:10 SMART Link no. 1 Discharge temperature above alarm limit | 0 | 1 |  |  | 1.27
1x1711 | Active alarm 1211 | Alarm 81:11 SMART Link no. 1 Pressure difference below alarm limit | 0 | 1 |  |  | 1.27
1x1712 | Active alarm 1212 |  | 0 | 1
1x1713 | Active alarm 1213 |  | 0 | 1
1x1714 | Active alarm 1214 |  | 0 | 1
1x1715 | Active alarm 1215 |  | 0 | 1
1x1716 | Active alarm 1216 |  | 0 | 1
1x1717 | Active alarm 1217 | Alarm 82:2 SMART Link no. 2 supply air flow below defrost alarm limit | 0 | 1 |  |  | 1.25
1x1718 | Active alarm 1218 | Alarm 82:3 SMART Link no. 2 High pressure switch tripped | 0 | 1 |  |  | 1.27
1x1719 | Active alarm 1219 | Alarm 82:4 SMART Link no. 2 High pressure above alarm limit | 0 | 1 |  |  | 1.27
1x1720 | Active alarm 1220 | Alarm 82:5 SMART Link no. 2 Low pressure below alarm limit | 0 | 1 |  |  | 1.27
1x1721 | Active alarm 1221 | Alarm 82:6 SMART Link no. 2 Evaporation temperature below alarm limit | 0 | 1 |  |  | 1.27
1x1722 | Active alarm 1222 | Alarm 82:7 SMART Link no. 2 Inverter group alarm (Power+) | 0 | 1 |  |  | 1.27
1x1723 | Active alarm 1223 | Alarm 82:8 SMART Link no. 2 Envelope alarm | 0 | 1 |  |  | 1.27
1x1724 | Active alarm 1224 | Alarm 82:9 SMART Link no. 2 Starting up of faulty compressor | 0 | 1 |  |  | 1.27
1x1725 | Active alarm 1225 | Alarm 82:10 SMART Link no. 2 Discharge temperature above alarm limit | 0 | 1 |  |  | 1.27
1x1726 | Active alarm 1226 | Alarm 82:11 SMART Link no. 2 Pressure difference below alarm limit | 0 | 1 |  |  | 1.27
1x1727 | Active alarm 1227 |  | 0 | 1
1x1728 | Active alarm 1228 |  | 0 | 1
1x1729 | Active alarm 1229 |  | 0 | 1
1x1730 | Active alarm 1230 |  | 0 | 1
1x1731 | Active alarm 1231 |  | 0 | 1
1x1732 | Active alarm 1232 | Alarm 83:2 SMART Link no. 3 supply air flow below defrost alarm limit | 0 | 1 |  |  | 1.25
1x1733 | Active alarm 1233 | Alarm 83:3 SMART Link no. 3 High pressure switch tripped | 0 | 1 |  |  | 1.27
1x1734 | Active alarm 1234 | Alarm 83:4 SMART Link no. 3 High pressure above alarm limit | 0 | 1 |  |  | 1.27
1x1735 | Active alarm 1235 | Alarm 83:5 SMART Link no. 3 Low pressure below alarm limit | 0 | 1 |  |  | 1.27
1x1736 | Active alarm 1236 | Alarm 83:6 SMART Link no. 3 Evaporation temperature below alarm limit | 0 | 1 |  |  | 1.27
1x1737 | Active alarm 1237 | Alarm 83:7 SMART Link no. 3 Inverter group alarm (Power+) | 0 | 1 |  |  | 1.27
1x1738 | Active alarm 1238 | Alarm 83:8 SMART Link no. 3 Envelope alarm | 0 | 1 |  |  | 1.27
1x1739 | Active alarm 1239 | Alarm 83:9 SMART Link no. 3 Starting up of faulty compressor | 0 | 1 |  |  | 1.27
1x1740 | Active alarm 1240 | Alarm 83:10 SMART Link no. 3 Discharge temperature above alarm limit | 0 | 1 |  |  | 1.27
1x1741 | Active alarm 1241 | Alarm 83:11 SMART Link no. 3 Pressure difference below alarm limit | 0 | 1 |  |  | 1.27
1x1742 | Active alarm 1242 |  | 0 | 1
1x1743 | Active alarm 1243 |  | 0 | 1
1x1744 | Active alarm 1244 |  | 0 | 1
1x1745 | Active alarm 1245 |  | 0 | 1
1x1746 | Active alarm 1246 |  | 0 | 1
1x1747 | Active alarm 1247 | Alarm 84:2 SMART Link no. 4 supply air flow below defrost alarm limit | 0 | 1 |  |  | 1.25
1x1748 | Active alarm 1248 | Alarm 84:3 SMART Link no. 4 High pressure switch tripped | 0 | 1 |  |  | 1.27
1x1749 | Active alarm 1249 | Alarm 84:4 SMART Link no. 4 High pressure above alarm limit | 0 | 1 |  |  | 1.27
1x1750 | Active alarm 1250 | Alarm 84:5 SMART Link no. 4 Low pressure below alarm limit | 0 | 1 |  |  | 1.27
1x1751 | Active alarm 1251 | Alarm 84:6 SMART Link no. 4 Evaporation temperature below alarm limit | 0 | 1 |  |  | 1.27
1x1752 | Active alarm 1252 | Alarm 84:7 SMART Link no. 4 Inverter group alarm (Power+) | 0 | 1 |  |  | 1.27
1x1753 | Active alarm 1253 | Alarm 84:8 SMART Link no. 4 Envelope alarm | 0 | 1 |  |  | 1.27
1x1754 | Active alarm 1254 | Alarm 84:9 SMART Link no. 4 Starting up of faulty compressor | 0 | 1 |  |  | 1.27
1x1755 | Active alarm 1255 | Alarm 84:10 SMART Link no. 4 Discharge temperature above alarm limit | 0 | 1 |  |  | 1.27
1x1756 | Active alarm 1256 | Alarm 84:11 SMART Link no. 4 Pressure difference below alarm limit | 0 | 1 |  |  | 1.27
1x1757 | Active alarm 1257 |  | 0 | 1
1x1758 | Active alarm 1258 |  | 0 | 1
1x1759 | Active alarm 1259 |  | 0 | 1
1x1760 | Active alarm 1260 |  | 0 | 1
1x1761 | Active alarm 1261 |  | 0 | 1
1x1762 | Active alarm 1262 |  | 0 | 1
1x1763 | Active alarm 1263 |  | 0 | 1
1x1764 | Active alarm 1264 |  | 0 | 1
1x1765 | Active alarm 1265 |  | 0 | 1
1x1766 | Active alarm 1266 |  | 0 | 1
1x1767 | Active alarm 1267 |  | 0 | 1
1x1768 | Active alarm 1268 |  | 0 | 1
1x1769 | Active alarm 1269 |  | 0 | 1
1x1770 | Active alarm 1270 |  | 0 | 1
1x1771 | Active alarm 1271 |  | 0 | 1
1x1772 | Active alarm 1272 |  | 0 | 1
1x1773 | Active alarm 1273 |  | 0 | 1
1x1774 | Active alarm 1274 |  | 0 | 1
1x1775 | Active alarm 1275 |  | 0 | 1
1x1776 | Active alarm 1276 |  | 0 | 1
1x1777 | Active alarm 1277 |  | 0 | 1
1x1778 | Active alarm 1278 |  | 0 | 1
1x1779 | Active alarm 1279 |  | 0 | 1
1x1780 | Active alarm 1280 |  | 0 | 1
1x1781 | Active alarm 1281 |  | 0 | 1
1x1782 | Active alarm 1282 |  | 0 | 1
1x1783 | Active alarm 1283 |  | 0 | 1
1x1784 | Active alarm 1284 |  | 0 | 1
1x1785 | Active alarm 1285 |  | 0 | 1
1x1786 | Active alarm 1286 |  | 0 | 1
1x1787 | Active alarm 1287 |  | 0 | 1
1x1788 | Active alarm 1288 |  | 0 | 1
1x1789 | Active alarm 1289 |  | 0 | 1
1x1790 | Active alarm 1290 |  | 0 | 1
1x1791 | Active alarm 1291 |  | 0 | 1
1x1792 | Active alarm 1292 |  | 0 | 1
1x1793 | Active alarm 1293 |  | 0 | 1
1x1794 | Active alarm 1294 |  | 0 | 1
1x1795 | Active alarm 1295 |  | 0 | 1
1x1796 | Active alarm 1296 |  | 0 | 1
1x1797 | Active alarm 1297 |  | 0 | 1
1x1798 | Active alarm 1298 |  | 0 | 1
1x1799 | Active alarm 1299 |  | 0 | 1
1x1800 | Active alarm 1300 |  | 0 | 1
1x1801 | Active alarm 1301 |  | 0 | 1
1x1802 | Active alarm 1302 |  | 0 | 1
1x1803 | Active alarm 1303 |  | 0 | 1
1x1804 | Active alarm 1304 |  | 0 | 1
1x1805 | Active alarm 1305 |  | 0 | 1
1x1806 | Active alarm 1306 |  | 0 | 1
1x1807 | Active alarm 1307 |  | 0 | 1
1x1808 | Active alarm 1308 |  | 0 | 1
1x1809 | Active alarm 1309 |  | 0 | 1
1x1810 | Active alarm 1310 |  | 0 | 1
1x1811 | Active alarm 1311 |  | 0 | 1
1x1812 | Active alarm 1312 |  | 0 | 1
1x1813 | Active alarm 1313 |  | 0 | 1
1x1814 | Active alarm 1314 |  | 0 | 1
1x1815 | Active alarm 1315 |  | 0 | 1
1x1816 | Active alarm 1316 |  | 0 | 1
1x1817 | Active alarm 1317 |  | 0 | 1
1x1818 | Active alarm 1318 |  | 0 | 1
1x1819 | Active alarm 1319 |  | 0 | 1
1x1820 | Active alarm 1320 |  | 0 | 1
1x1821 | Active alarm 1321 |  | 0 | 1
1x1822 | Active alarm 1322 |  | 0 | 1
1x1823 | Active alarm 1323 |  | 0 | 1
1x1824 | Active alarm 1324 |  | 0 | 1
1x1825 | Active alarm 1325 |  | 0 | 1
1x1826 | Active alarm 1326 |  | 0 | 1
1x1827 | Active alarm 1327 |  | 0 | 1
1x1828 | Active alarm 1328 |  | 0 | 1
1x1829 | Active alarm 1329 |  | 0 | 1
1x1830 | Active alarm 1330 |  | 0 | 1
1x1831 | Active alarm 1331 |  | 0 | 1
1x1832 | Active alarm 1332 |  | 0 | 1
1x1833 | Active alarm 1333 |  | 0 | 1
1x1834 | Active alarm 1334 |  | 0 | 1
1x1835 | Active alarm 1335 |  | 0 | 1
1x1836 | Active alarm 1336 |  | 0 | 1
1x1837 | Active alarm 1337 |  | 0 | 1
1x1838 | Active alarm 1338 |  | 0 | 1
1x1839 | Active alarm 1339 |  | 0 | 1
1x1840 | Active alarm 1340 |  | 0 | 1
1x1841 | Active alarm 1341 |  | 0 | 1
1x1842 | Active alarm 1342 |  | 0 | 1
1x1843 | Active alarm 1343 |  | 0 | 1
1x1844 | Active alarm 1344 |  | 0 | 1
1x1845 | Active alarm 1345 |  | 0 | 1
1x1846 | Active alarm 1346 |  | 0 | 1
1x1847 | Active alarm 1347 |  | 0 | 1
1x1848 | Active alarm 1348 |  | 0 | 1
1x1849 | Active alarm 1349 |  | 0 | 1
1x1850 | Active alarm 1350 |  | 0 | 1
1x1851 | Active alarm 1351 |  | 0 | 1
1x1852 | Active alarm 1352 |  | 0 | 1
1x1853 | Active alarm 1353 |  | 0 | 1
1x1854 | Active alarm 1354 |  | 0 | 1
1x1855 | Active alarm 1355 |  | 0 | 1
1x1856 | Active alarm 1356 |  | 0 | 1
1x1857 | Active alarm 1357 |  | 0 | 1
1x1858 | Active alarm 1358 |  | 0 | 1
1x1859 | Active alarm 1359 |  | 0 | 1
1x1860 | Active alarm 1360 |  | 0 | 1
1x1861 | Active alarm 1361 |  | 0 | 1
1x1862 | Active alarm 1362 |  | 0 | 1
1x1863 | Active alarm 1363 |  | 0 | 1
1x1864 | Active alarm 1364 |  | 0 | 1
1x1865 | Active alarm 1365 |  | 0 | 1
1x1866 | Active alarm 1366 |  | 0 | 1
1x1867 | Active alarm 1367 |  | 0 | 1
1x1868 | Active alarm 1368 |  | 0 | 1
1x1869 | Active alarm 1369 |  | 0 | 1
1x1870 | Active alarm 1370 |  | 0 | 1
1x1871 | Active alarm 1371 |  | 0 | 1
1x1872 | Active alarm 1372 |  | 0 | 1
1x1873 | Active alarm 1373 |  | 0 | 1
1x1874 | Active alarm 1374 |  | 0 | 1
1x1875 | Active alarm 1375 |  | 0 | 1
1x1876 | Active alarm 1376 |  | 0 | 1
1x1877 | Active alarm 1377 |  | 0 | 1
1x1878 | Active alarm 1378 |  | 0 | 1
1x1879 | Active alarm 1379 |  | 0 | 1
1x1880 | Active alarm 1380 |  | 0 | 1
1x1881 | Active alarm 1381 |  | 0 | 1
1x1882 | Active alarm 1382 |  | 0 | 1
1x1883 | Active alarm 1383 |  | 0 | 1
1x1884 | Active alarm 1384 |  | 0 | 1
1x1885 | Active alarm 1385 |  | 0 | 1
1x1886 | Active alarm 1386 |  | 0 | 1
1x1887 | Active alarm 1387 |  | 0 | 1
1x1888 | Active alarm 1388 |  | 0 | 1
1x1889 | Active alarm 1389 |  | 0 | 1
1x1890 | Active alarm 1390 |  | 0 | 1
1x1891 | Active alarm 1391 |  | 0 | 1
1x1892 | Active alarm 1392 |  | 0 | 1
1x1893 | Active alarm 1393 |  | 0 | 1
1x1894 | Active alarm 1394 |  | 0 | 1
1x1895 | Active alarm 1395 |  | 0 | 1
1x1896 | Active alarm 1396 |  | 0 | 1
1x1897 | Active alarm 1397 |  | 0 | 1
1x1898 | Active alarm 1398 |  | 0 | 1
1x1899 | Active alarm 1399 |  | 0 | 1
1x1900 | Active alarm 1400 |  | 0 | 1
1x1901 | Active alarm 1401 |  | 0 | 1
1x1902 | Active alarm 1402 |  | 0 | 1
1x1903 | Active alarm 1403 |  | 0 | 1
1x1904 | Active alarm 1404 |  | 0 | 1
1x1905 | Active alarm 1405 |  | 0 | 1
1x1906 | Active alarm 1406 |  | 0 | 1
1x1907 | Active alarm 1407 |  | 0 | 1
1x1908 | Active alarm 1408 |  | 0 | 1
1x1909 | Active alarm 1409 |  | 0 | 1
1x1910 | Active alarm 1410 |  | 0 | 1
1x1911 | Active alarm 1411 | Info 95:1 Supply air pre filter calibration performed at low air flow | 0 | 1 |  |  | 2.40
1x1912 | Active alarm 1412 | Info 95:2 Extract air pre filter calibration performed at low air flow | 0 | 1 |  |  | 2.40
1x1913 | Active alarm 1413 | Info 95:3 Supply air AHU filter calibration performed at low air flow | 0 | 1 |  |  | 2.40
1x1914 | Active alarm 1414 | Info 95:4 Extract air AHU filter calibration performed at low air flow | 0 | 1 |  |  | 2.40
1x1915 | Active alarm 1415 | Info 95:5 End filter calibration performed at low air flow | 0 | 1 |  |  | 2.40
1x1916 | Active alarm 1416 |  | 0 | 1
1x1917 | Active alarm 1417 |  | 0 | 1
1x1918 | Active alarm 1418 |  | 0 | 1
1x1919 | Active alarm 1419 |  | 0 | 1
1x1920 | Active alarm 1420 |  | 0 | 1
1x1921 | Active alarm 1421 |  | 0 | 1
1x1922 | Active alarm 1422 |  | 0 | 1
1x1923 | Active alarm 1423 |  | 0 | 1
1x1924 | Active alarm 1424 | Info 95:14 Reduced humidity recovery time above alarm limit | 0 | 1 |  |  | 2.43
1x1925 | Active alarm 1425 | Info 95:15 Supply air humidity level above outdoor air level | 0 | 1 |  |  | 2.43
1x1926 | Active alarm 1426 | Info 96:1 H/C defrost calibration not performed | 0 | 1 |  |  | 1.27
1x1927 | Active alarm 1427 | Info 96:2 H/C defrost calibration not approved | 0 | 1 |  |  | 1.27
1x1928 | Active alarm 1428 | Info 96:3 H/C minimum SA flow limit below factory setting | 0 | 1 |  |  | 1.27
1x1929 | Active alarm 1429 | Info 96:4 H/C minimum EA flow limit below factory setting | 0 | 1 |  |  | 1.27
1x1930 | Active alarm 1430 | Info 96:5 H/C OA temp limit for heating below factory setting | 0 | 1 |  |  | 1.27
1x1931 | Active alarm 1431 |  | 0 | 1
1x1932 | Active alarm 1432 |  | 0 | 1
1x1933 | Active alarm 1433 |  | 0 | 1
1x1934 | Active alarm 1434 |  | 0 | 1
1x1935 | Active alarm 1435 |  | 0 | 1
1x1936 | Active alarm 1436 |  | 0 | 1
1x1937 | Active alarm 1437 |  | 0 | 1
1x1938 | Active alarm 1438 |  | 0 | 1
1x1939 | Active alarm 1439 |  | 0 | 1
1x1940 | Active alarm 1440 |  | 0 | 1
1x1941 | Active alarm 1441 | Info 97:1 Cloud connection offline | 0 | 1 |  |  | 2.42
1x1942 | Active alarm 1442 | Info 97:2 Cloud certificate missing/expired | 0 | 1 |  |  | 2.42
1x1943 | Active alarm 1443 |  | 0 | 1
1x1944 | Active alarm 1444 |  | 0 | 1
1x1945 | Active alarm 1445 |  | 0 | 1
1x1946 | Active alarm 1446 |  | 0 | 1
1x1947 | Active alarm 1447 |  | 0 | 1
1x1948 | Active alarm 1448 |  | 0 | 1
1x1949 | Active alarm 1449 |  | 0 | 1
1x1950 | Active alarm 1450 |  | 0 | 1
1x1951 | Active alarm 1451 |  | 0 | 1
1x1952 | Active alarm 1452 | Info 97:12 Plate heat exchanger bypass optimization not performed | 0 | 1 |  |  | 1.13
1x1953 | Active alarm 1453 | Info 97:13 Plate heat exchanger bypass optimization not approved | 0 | 1 |  |  | 1.13
1x1954 | Active alarm 1454 | Info 97:14 Plate heat exchanger defrost calibration not performed | 0 | 1 |  |  | 1.13
1x1955 | Active alarm 1455 | Info 97:15 Plate heat exchanger defrost calibration not approved | 0 | 1 |  |  | 1.13
1x1956 | Active alarm 1456 | Info 98:1 Supply air pre-filter calibration not performed | 0 | 1
1x1957 | Active alarm 1457 | Info 98:2 Supply air pre-filter calibration not approved | 0 | 1
1x1958 | Active alarm 1458 | Info 98:3 Extract air pre-filter calibration not performed | 0 | 1
1x1959 | Active alarm 1459 | Info 98:4 Extract air pre-filter calibration not approved | 0 | 1
1x1960 | Active alarm 1460 | Info 98:5 Supply air air handling unit filter calibration not performed | 0 | 1
1x1961 | Active alarm 1461 | Info 98:6 Supply air air handling unit filter calibration not approved | 0 | 1
1x1962 | Active alarm 1462 | Info 98:7 Extract air air handling unit filter calibration not performed | 0 | 1
1x1963 | Active alarm 1463 | Info 98:8 Extract air air handling unit filter calibration not approved | 0 | 1
1x1964 | Active alarm 1464 | Info 98:9 Supply air end filter calibration not performed | 0 | 1
1x1965 | Active alarm 1465 | Info 98:10 Supply air end filter calibration not approved | 0 | 1
1x1966 | Active alarm 1466 | Info 98:11 Rotary heat exchanger defrost calibration not performed | 0 | 1
1x1967 | Active alarm 1467 | Info 98:12 Rotary heat exchanger defrost calibration not approved | 0 | 1
1x1968 | Active alarm 1468 | Info 98:13 ReCO2 calibration not performed | 0 | 1
1x1969 | Active alarm 1469 | Info 98:14 ReCO2 calibration not approved | 0 | 1
1x1970 | Active alarm 1470 | Info 98:15 ReCO2 incorrect setting | 0 | 1
1x1971 | Active alarm 1471 | Info 99:1 E-mail error | 0 | 1
1x1972 | Active alarm 1472 |  | 0 | 1
1x1973 | Active alarm 1473 |  | 0 | 1
1x1974 | Active alarm 1474 |  | 0 | 1
1x1975 | Active alarm 1475 | Info 99:5 FTP error | 0 | 1 |  |  | 1.19
1x1976 | Active alarm 1476 | Info 99:6 Schedule invalid data auto corrected | 0 | 1 |  |  | 2.36
1x1977 | Active alarm 1477 | Info 99:7 SD card memory soon full. Oldest log data will soon be deleted | 0 | 1
1x1978 | Active alarm 1478 | Info 99:8 SD card memory full. Oldest log data deleted | 0 | 1
1x1979 | Active alarm 1479 | Info 99:9 IQlogic CPU2 reboot caused by corrupt SD card remove and replace | 0 | 1 |  |  | 2.42
1x1980 | Active alarm 1480 |  | 0 | 1
1x1981 | Active alarm 1481 | Info 99:11 No external outdoor air temperature sensor connected for heat retention | 0 | 1 |  |  | 1.26
1x1982 | Active alarm 1482 | Info 99:12 No extract air/room temperature sensor connected | 0 | 1 |  |  | 1.32
1x1983 | Active alarm 1483 |  | 0 | 1
1x1984 | Active alarm 1484 | Info 99:14 Internal serial memory error CPU 1 | 0 | 1
1x1985 | Active alarm 1485 | Info 99:15 Clock circuit defective | 0 | 1
1x1986 | Active alarm 1486 |  | 0 | 1
1x1987 | Active alarm 1487 |  | 0 | 1
1x1988 | Active alarm 1488 |  | 0 | 1
1x1989 | Active alarm 1489 |  | 0 | 1
1x1990 | Active alarm 1490 |  | 0 | 1
1x1991 | Active alarm 1491 |  | 0 | 1
1x1992 | Active alarm 1492 |  | 0 | 1
1x1993 | Active alarm 1493 |  | 0 | 1
1x1994 | Active alarm 1494 |  | 0 | 1
1x1995 | Active alarm 1495 |  | 0 | 1
1x1996 | Active alarm 1496 |  | 0 | 1
1x1997 | Active alarm 1497 |  | 0 | 1
1x1998 | Active alarm 1498 |  | 0 | 1
1x1999 | Active alarm 1499 |  | 0 | 1
1x2000 | Active alarm 1500 |  | 0 | 1
1x2001 | Active alarm group 1 |  | 0 | 1
1x2002 | Active alarm group 2 |  | 0 | 1
1x2003 | Active alarm group 3 |  | 0 | 1
1x2004 | Active alarm group 4 |  | 0 | 1
1x2005 | Active alarm group 5 |  | 0 | 1
1x2006 | Active alarm group 6 |  | 0 | 1
1x2007 | Active alarm group 7 |  | 0 | 1
1x2008 | Active alarm group 8 |  | 0 | 1
1x2009 | Active alarm group 9 |  | 0 | 1
1x2010 | Active alarm group 10 |  | 0 | 1
1x2011 | Active alarm group 11 |  | 0 | 1
1x2012 | Active alarm group 12 |  | 0 | 1
1x2013 | Active alarm group 13 |  | 0 | 1
1x2014 | Active alarm group 14 |  | 0 | 1
1x2015 | Active alarm group 15 |  | 0 | 1
1x2016 | Active alarm group 16 |  | 0 | 1
1x2017 | Active alarm group 17 |  | 0 | 1
1x2018 | Active alarm group 18 |  | 0 | 1
1x2019 | Active alarm group 19 |  | 0 | 1
1x2020 | Active alarm group 20 |  | 0 | 1
1x2021 | Active alarm group 21 |  | 0 | 1
1x2022 | Active alarm group 22 |  | 0 | 1
1x2023 | Active alarm group 23 |  | 0 | 1
1x2024 | Active alarm group 24 |  | 0 | 1
1x2025 | Active alarm group 25 |  | 0 | 1
1x2026 | Active alarm group 26 |  | 0 | 1
1x2027 | Active alarm group 27 |  | 0 | 1
1x2028 | Active alarm group 28 |  | 0 | 1
1x2029 | Active alarm group 29 |  | 0 | 1
1x2030 | Active alarm group 30 |  | 0 | 1
1x2031 | Active alarm group 31 |  | 0 | 1
1x2032 | Active alarm group 32 |  | 0 | 1
1x2033 | Active alarm group 33 |  | 0 | 1
1x2034 | Active alarm group 34 |  | 0 | 1
1x2035 | Active alarm group 35 |  | 0 | 1
1x2036 | Active alarm group 36 |  | 0 | 1
1x2037 | Active alarm group 37 |  | 0 | 1
1x2038 | Active alarm group 38 |  | 0 | 1
1x2039 | Active alarm group 39 |  | 0 | 1
1x2040 | Active alarm group 40 |  | 0 | 1
1x2041 | Active alarm group 41 |  | 0 | 1
1x2042 | Active alarm group 42 |  | 0 | 1
1x2043 | Active alarm group 43 |  | 0 | 1
1x2044 | Active alarm group 44 |  | 0 | 1
1x2045 | Active alarm group 45 |  | 0 | 1
1x2046 | Active alarm group 46 |  | 0 | 1
1x2047 | Active alarm group 47 |  | 0 | 1
1x2048 | Active alarm group 48 |  | 0 | 1
1x2049 | Active alarm group 49 |  | 0 | 1
1x2050 | Active alarm group 50 |  | 0 | 1
1x2051 | Active alarm group 51 |  | 0 | 1
1x2052 | Active alarm group 52 |  | 0 | 1
1x2053 | Active alarm group 53 |  | 0 | 1
1x2054 | Active alarm group 54 |  | 0 | 1
1x2055 | Active alarm group 55 |  | 0 | 1
1x2056 | Active alarm group 56 |  | 0 | 1
1x2057 | Active alarm group 57 |  | 0 | 1
1x2058 | Active alarm group 58 |  | 0 | 1
1x2059 | Active alarm group 59 |  | 0 | 1
1x2060 | Active alarm group 60 |  | 0 | 1
1x2061 | Active alarm group 61 |  | 0 | 1
1x2062 | Active alarm group 62 |  | 0 | 1
1x2063 | Active alarm group 63 |  | 0 | 1
1x2064 | Active alarm group 64 |  | 0 | 1
1x2065 | Active alarm group 65 |  | 0 | 1
1x2066 | Active alarm group 66 |  | 0 | 1
1x2067 | Active alarm group 67 |  | 0 | 1
1x2068 | Active alarm group 68 |  | 0 | 1
1x2069 | Active alarm group 69 |  | 0 | 1
1x2070 | Active alarm group 70 |  | 0 | 1
1x2071 | Active alarm group 71 |  | 0 | 1
1x2072 | Active alarm group 72 |  | 0 | 1
1x2073 | Active alarm group 73 |  | 0 | 1
1x2074 | Active alarm group 74 |  | 0 | 1
1x2075 | Active alarm group 75 |  | 0 | 1
1x2076 | Active alarm group 76 |  | 0 | 1
1x2077 | Active alarm group 77 |  | 0 | 1
1x2078 | Active alarm group 78 |  | 0 | 1
1x2079 | Active alarm group 79 |  | 0 | 1
1x2080 | Active alarm group 80 |  | 0 | 1
1x2081 | Active alarm group 81 |  | 0 | 1
1x2082 | Active alarm group 82 |  | 0 | 1
1x2083 | Active alarm group 83 |  | 0 | 1
1x2084 | Active alarm group 84 |  | 0 | 1
1x2085 | Active alarm group 85 |  | 0 | 1
1x2086 | Active alarm group 86 |  | 0 | 1
1x2087 | Active alarm group 87 |  | 0 | 1
1x2088 | Active alarm group 88 |  | 0 | 1
1x2089 | Active alarm group 89 |  | 0 | 1
1x2090 | Active alarm group 90 |  | 0 | 1
1x2091 | Active alarm group 91 |  | 0 | 1
1x2092 | Active alarm group 92 |  | 0 | 1
1x2093 | Active alarm group 93 |  | 0 | 1
1x2094 | Active alarm group 94 |  | 0 | 1
1x2095 | Active alarm group 95 |  | 0 | 1
1x2096 | Active alarm group 96 |  | 0 | 1
1x2097 | Active alarm group 97 |  | 0 | 1
1x2098 | Active alarm group 98 |  | 0 | 1
1x2099 | Active alarm group 99 |  | 0 | 1
1x2100 | Active alarm group 100 |  | 0 | 1

## Input Registers
GOLD_E_F_Modbus_260227
Input Registers. 16-bit integer value (RO).
Modbus | Name | Description | Min | Max | Unit | Default | Misc
AHU Air flow/duct pressure
3x0001 | Component name | 25=IQlogic | 0 | 999
3x0002 | Application id/AHU Type | 10=GOLD RX, 11=GOLD PX, 12=GOLD CX, 13=GOLD SD/SA,14=GOLD SD/EA, 15=GOLD SD/SA+CX, 16=GOLD SD/SA+EA, 17=GOLD SD/SA+EA+CX | 0 | 999
3x0003 | Air flow direction | 0=Fan no.2 as SA, 1=Fan no.1 as SA. | 0 | 1
Air flow regulation
3x0004 | SA Air flow | Present supply air flow. | 0 | 20000 | l/s
3x0005 | SA Air flow regulator | Present supply air flow regulator set point. | 0 | 20000 | l/s
3x0006 | EA Air flow | Present extract air flow. | 0 | 20000 | l/s
3x0007 | EA Air flow regulator | Present extract air flow regulator set point. | 0 | 20000 | l/s
Pressure regulation
3x0008 | SA Duct pressure | Present supply air duct pressure. | 0.0 | 2000.0 | Pa
3x0009 | SA Duct pressure regulator | Present supply air duct pressure regulator set point. | 0.0 | 2000.0 | Pa
3x0010 | EA Duct pressure | Present extract air duct pressure. | 0.0 | 2000.0 | Pa
3x0011 | EA Duct pressure regulator | Present extract air duct pressure regulator set point. | 0.0 | 2000.0 | Pa
Demand regulation
3x0012 | Demand input level | Present input signal for demand regulation. | 0.00 | 100.00 | %
3x0013 | Demand regulator | Present demand regulator set point. | 0.00 | 100.00 | %
Air flow pressure sensors
3x0014 | SA Air flow pressure | Present air flow pressure in the supply air fan inlet. | 0.0 | 2000.0 | Pa
3x0015 | EA Air flow pressure | Present air flow pressure in the extract air fan inlet. | 0.0 | 2000.0 | Pa
3x0016
3x0017
Demand regulation
3x0018 | Demand CO2 regulator | Present demand CO2 regulator set point. | 0 | 10000 | ppm |  | 1.23
3x0019 | Demand VOC regulator | Present demand VOC regulator set point. | 0 | 10000 | ppm |  | 1.23
3x0020
3x0021
3x0022
Filters
3x0023 | SA Pre-filter pressure level | Present supply air pre-filter pressure drop. | 0.0 | 2000.0 | Pa
3x0024 | SA Pre-filter pressure alarm limit | Present supply air pre-filter pressure alarm limit. | 0.0 | 2000.0 | Pa
3x0025 | EA Pre-filter pressure level | Present extract air pre-filter pressure drop. | 0.0 | 2000.0 | Pa
3x0026 | EA Pre-filter pressure alarm limit | Present extract air pre-filter pressure alarm limit. | 0.0 | 2000.0 | Pa
3x0027 | SA AHU filter pressure level | Present supply air filter pressure drop. | 0.0 | 2000.0 | Pa
3x0028 | SA AHU filter pressure alarm limit | Present supply air filter pressure alarm limit. | 0.0 | 2000.0 | Pa
3x0029 | EA AHU filter pressure level | Present extract air filter pressure drop. | 0.0 | 2000.0 | Pa
3x0030 | EA AHU filter pressure alarm limit | Present extract air filter pressure alarm limit. | 0.0 | 2000.0 | Pa
3x0031 | SA End-filter pressure level | Present supply air end-filter pressure drop. | 0.0 | 2000.0 | Pa
3x0032 | SA End-filter pressure alarm limit | Present supply air end-filter pressure alarm limit. | 0.0 | 2000.0 | Pa
3x0033
3x0034
3x0035
3x0036
Fans
3x0037 | SA Fan level | Present fan speed level of the supply air fan. | 0.00 | 100.00 | %
3x0038 | EA Fan level | Present fan speed level of the extract air fan. | 0.00 | 100.00 | %
3x0039 | SA Fan speed | Present fan speed level of the supply air fan. | 0 | 4000 | rpm
3x0040 | EA Fan speed | Present fan speed level of the extract air fan. | 0 | 4000 | rpm
3x0041 | SA Voltage | Present voltage level of the supply air fan. | 0 | 500 | V
3x0042 | EA Voltage | Present voltage level of the extract air fan. | 0 | 500 | V
3x0043 | SA Fan current | Present current level of the supply air fans. Includes all supply air fans. | 0 | 32.700 | A
3x0044 | EA Fan current | Present current level of the extract air fans. Includes all supply air fans. | 0 | 32.700 | A
3x0045 | SA Fan power | Present power level of the supply air fans. Includes all supply air fans. | 0 | 45.000 | kW
3x0046 | EA Fan power | Present power consumption level of the extract air fans. Includes all extract air fans. | 0 | 45.000 | kW
3x0047 | SA Fan kWh | Total power consumption of the supply air fans. Includes all supply air fans. | 0 | 9999 | kWh
3x0048 | EA Fan kWh | Total power consumption level of the extract air fans. Includes all extract air fans. | 0 | 9999 | kWh
3x0049 | SA Fan MWh | Total power consumption of the supply air fans. Includes all supply air fans. | 0 | 9999 | MWh
3x0050 | EA Fan MWh | Total power consumption level of the extract air fans. Includes all extract air fans. | 0 | 9999 | MWh
3x0051 | SA Fan operation time | Total operation time of the supply air fan presented in days (24h). | 0 | 30000 | days
3x0052 | EA Fan operation time | Total operation time of the extract air fan presented in days (24h). | 0 | 30000 | days
3x0053
3x0054
3x0055 | SA Fan min air flow | Supply air AHU min air flow | 0 | 18000 | l/s
3x0056 | EA Fan min air flow | Extract air AHU min air flow | 0 | 18000 | l/s
3x0057 | SA Fan max air flow | Supply air AHU max air flow | 0 | 18000 | l/s
3x0058 | EA Fan max air flow | Extract air AHU max air flow | 0 | 18000 | l/s
3x0059
3x0060
3x0061
3x0062
3x0063 | SFP | Calculated SFP level. | 0.00 | 100.00 | kW/m3/s
AHU Temperature sensors
3x0064 | SA Temperature | Present supply air temperature. | -55.00 | 125.00 | °C
3x0065 | SA-D Temperature | Present supply air density temperature. | -55.00 | 125.00 | °C
3x0066 | EA Temperature RX | Present extract air temperature in the unit (only AHU type RX). | -55.00 | 125.00 | °C
3x0067 | EA-D Temperature | Present extract air density temperature. | -55.00 | 125.00 | °C
3x0068 | EA Regulation temperature | Present extract air temperature used for regulation. | -55.00 | 125.00 | °C
3x0069 | EA Temperature PX/CX | Present extract air temperature in the unit (only AHU type PX/CX). | -55.00 | 125.00 | °C |  | 1.13
3x0070 | EA Temperature SD | Present extract air temperature in the unit (only AHU type SD). | -55.00 | 125.00 | °C |  | 1.13
3x0071
3x0072 | Outdoor temperature COOL DX | Present outdoor air temperature in the COOL DX unit. | -55.00 | 125.00 | °C |  | 1.13
3x0073 | Outdoor temperature | Present outdoor air temperature in the unit. | -55.00 | 125.00 | °C
3x0074 | Outdoor regulation temperature | Present outdoor air temperature used for regulation. | -55.00 | 125.00 | °C
3x0075 | External outdoor temperature 1 | Present external outdoor temperature of sensor 1. | -55.00 | 125.00 | °C
3x0076 | External outdoor temperature 2 | Present external outdoor temperature of sensor 2. | -55.00 | 125.00 | °C
3x0077 | External outdoor temperature 3 | Present external outdoor temperature of sensor 3. | -55.00 | 125.00 | °C
3x0078 | External outdoor temperature 4 | Present external outdoor temperature of sensor 4. | -55.00 | 125.00 | °C
3x0079 | External outdoor temperature min/max/average | Present calculated min, max or average (depending of configuration) temperature of outd. sensor 1-4. | -55.00 | 125.00 | °C
3x0080 | EA duct temperature | Present extract air duct air temperature. | -55.00 | 125.00 | °C |  | 1.12
3x0081 | Room temperature 1 | Present room temperature of sensor 1. | -55.00 | 125.00 | °C
3x0082 | Room temperature 2 | Present room temperature of sensor 2. | -55.00 | 125.00 | °C
3x0083 | Room temperature 3 | Present room temperature of sensor 3. | -55.00 | 125.00 | °C
3x0084 | Room temperature 4 | Present room temperature of sensor 4. | -55.00 | 125.00 | °C
3x0085 | Room temperature min/max/average | Present calculated min, max or average (depending of configuration) temperature of room sensor 1-4. | -55.00 | 125.00 | °C
3x0086
AHU Temperature regulation
3x0087 | SA Temp regulator | Present supply air temperature regulator set point. | 0.00 | 50.00 | °C
3x0088 | EA Temp regulator | Present extract air temperature regulator set point. | 0.00 | 50.00 | °C
3x0089
3x0090 | Cool exchanger regulator level | Present operation level of cool recovery. | 0.00 | 100.00 | % |  | 1.11
3x0091 | Heat exchanger regulator level | Present operation level of heat recovery. | 0.00 | 100.00 | %
3x0092 | Extra regulation sequence 1 heat regulator level | Present level of extra regulation heat. | 0.00 | 100.00 | %
3x0093 | Extra regulation sequence 1 heat output level |  | 0.00 | 100.00 | %
3x0094 | Reheat regulator level | Present level of reheat. | 0.00 | 100.00 | %
3x0095 | Reheat output level |  | 0.00 | 100.00 | %
3x0096 | ReCO2 heat level | Present level of ReCO2 heat. | 0.00 | 100.00 | %
3x0097 | Down regulation level | Present level of fan down regulation. | 0.00 | 100.00 | %
3x0098 | Heating boost level | Present level of heating boost. | 0.00 | 100.00 | %
3x0099 | Extra regulation sequence 1 cool regulator level | Present level of extra regulation cool. | 0.00 | 100.00 | %
3x0100 | Extra regulation sequence 1 cool output level | Present level of extra regulation cool. | 0.00 | 100.00 | %
3x0101 | Cool regulator level | Present level of cooling. | 0.00 | 100.00 | %
3x0102 | Cool output level | Present level of cooling. | 0.00 | 100.00 | %
3x0103 | ReCO2 cool level | Present level of ReCO2 heat. | 0.00 | 100.00 | %
3x0104 | Cooling boost level | Present level of cooling boost. | 0.00 | 100.00 | %
AHU heat exchange
3x0105 | RHX operation level | Present speed level of the rotary heat exchanger. | 0.00 | 100.00 | %
3x0106 | RHX/PHX/CHX efficiency | Calculated level of the heat exchanger efficiency. | 0.00 | 100.00 | % |  | 1.23
3x0107 | RHX defrost pressure level | Present pressure drop for the rotary heat exchanger. | 0.0 | 2000.0 | Pa
3x0108 | RHX defrost pressure alarm limit | Present pressure drop alarm limit for the rotary heat exchanger. | 0.0 | 2000.0 | Pa
3x0109 | RHX carry over control pressure level | Present pressure difference for the rotary heat exchangers purging sector. | 0.0 | 1000.0 | Pa
3x0110 | PHX bypass type | 0=Center, 1=Side | 0 | 1 |  |  | 2.43
3x0111 | RHX operation time | Total operation time of the rotary heat exchanger presented in days (24h). | 0 | 30000 | Days
3x0112 | PX exchanger bypass 4A output |  | 0.00 | 100.00 | % |  | 2.43
3x0113 | PX exchanger bypass 4A feedback |  | 0.00 | 100.00 | % |  | 2.43
3x0114 | PHX-2 3D Type | 0=Cross flow, 1=Counter flow | 0 | 1 |  |  | 1.21
3x0115 | PHX type | 0=PHX-1, one damper and humidity sensor, 1=PHX-2, three dampers, 2=PHX-3, one damper and pressure sensor. | 0 | 2 |  |  | 1.12
3x0116 | PHX-2/3 pressure drop level | Present pressure drop for the plate heat exchanger. | 0.0 | 2000.0 | Pa |  | 1.12
3x0117 | PHX-1 Bypass output | Present level of plate heat exchanger bypass output. | 0.00 | 100.00 | %
3x0118 | PHX-1 Bypass input | Present level of plate heat exchanger bypass input. | 0.00 | 100.00 | %
3x0119 | PHX-1 Bypass temperature 1 | Present bypass temperature sensor 1 in plate heat exchanger. | -55.00 | 125.00 | °C
3x0120 | PHX-1 Bypass temperature 2 | Present bypass temperature sensor 2 in plate heat exchanger. | -55.00 | 125.00 | °C
3x0121 | PHX-2 Damper 1 output | Present level of plate heat exchanger damper 1 output. | 0.00 | 100.00 | % |  | 1.12
3x0122 | PHX-2 Damper 1 input | Present level of plate heat exchanger damper 1 input. | 0.00 | 100.00 | % |  | 1.12
3x0123 | PHX-2 Damper 2 output | Present level of plate heat exchanger damper 2 output. | 0.00 | 100.00 | % |  | 1.12
3x0124 | PHX-2 Damper 2 input | Present level of plate heat exchanger damper 2 input. | 0.00 | 100.00 | % |  | 1.12
3x0125 | PHX-2 Bypass output | Present level of plate heat exchanger bypass output. | 0.00 | 100.00 | % |  | 1.12
3x0126 | PHX-2 Bypass input | Present level of plate heat exchanger bypass input. | 0.00 | 100.00 | % |  | 1.12
3x0127 | CHX-1 Valve output | Present level of coil heat exchanger valve output. | 0.00 | 100.00 | %
3x0128 | CHX-1 Valve input | Present level of coil heat exchanger valve input. | 0.00 | 100.00 | %
3x0129 | CHX-1 Return water temperature | Present return water temperature for coil heat exchanger. | -55.00 | 125.00 | °C
3x0130 | PHX/CHX operation time | Total operation time of the coil heat exchanger presented in days (24h). | 0 | 30000 | Days
3x0131
3x0132 | PHX-3 Bypass output | Present level of plate heat exchanger bypass output. | 0.00 | 100.00 | % |  | 1.12
3x0133 | PHX-3 Bypass input | Present level of plate heat exchanger bypass input. | 0.00 | 100.00 | % |  | 1.12
3x0134 | CHX-2 Return water temperature | Present return water temperature for coil heat exchanger. | -55.00 | 125.00 | °C |  | 1.18
3x0135 | CHX-2 Extract coil pressure level | Present extract coil differiential pressure. | 0 | 1600 | mBar |  | 1.18
3x0136 | PHX-1/2 /CHX Humidity level | Present level of air-humidity for calculation of bypass/valve limitation. | 0.00 | 100.00 | %
3x0137 | CHX-2 Valve output | Present level of coil heat exchanger valve output. | 0.00 | 100.00 | % |  | 1.18
3x0138 | CHX-2 Valve input | Present level of coil heat exchanger valve input. | 0.00 | 100.00 | % |  | 1.18
3x0139 | CHX-2 Pump output | Present level of pump heat exchanger output | 0.00 | 100.00 | % |  | 1.18
AHU Coils
3x0140 | Extra regulation sequence 1 coil type | 0=None,1..8=Electric, 9..10=Water, 11..15=Electric | 0 | 15
3x0141 | Extra regulation sequence 1 anti frost temp/overheat input | Present extra regulation anti frost temperature for water heat coil. Value 0=overheat when electric heat is used. | -55.00 | 125.00 | °C
3x0142 | Extra regulation sequence 2 coil type | 0=None,1..8=Electric, 9..10=Water, 11..15=Electric | 0 | 15 |  |  | 1.13
3x0143 | Extra regulation sequence 2 anti frost temp/overheat input | Present extra regulation anti frost temperature for water heat coil. Value 0=overheat when electric heat is used. | -55.00 | 125.00 | °C |  | 1.13
3x0144 | Extra regulation sequence 1 temperature guard |  | 0.00 | 100.00 | °C |  | 2.47
3x0145 | Extra regulation sequence 2 temperature guard |  | 0.00 | 100.00 | °C |  | 2.47
3x0146 | Extra regulation sequence 1 input level |  | 0.00 | 100.00 | %
3x0147 | Extra regulation sequence 1 heat operation time | Total operation time of extra regulation heat presented in days (24h). | 0 | 30000 | Days
3x0148 | Extra regulation sequence 1 cool operation time | Total operation time of extra regulation cool presented in days (24h). | 0 | 30000 | Days
3x0149 | Extra regulation sequence 2 input level |  | 0.00 | 100.00 | % |  | 1.13
3x0150 | Extra regulation sequence 2 heat operation time | Total operation time of extra regulation heat presented in days (24h). | 0 | 30000 | Days |  | 1.13
3x0151 | Extra regulation sequence 2 cool operation time | Total operation time of extra regulation cool presented in days (24h). | 0 | 30000 | Days |  | 1.13
3x0152 | Re-heat coil type | 0=None,1..8=Electric, 9..10=Water, 11..15=Electric | 0 | 15
3x0153 | Re-heat anti frost temp/overheat input | Present anti frost temperature for water heat coil. Value 0=overheat when electric heat is used. | -55.00 | 125.00 | °C
3x0154
3x0155
3x0156
3x0157
3x0158 | Re-heat input level |  | 0.00 | 100.00 | %
3x0159 | Re-heat operation time | Total operation time of re-heat presented in days (24h). | 0 | 30000 | Days
3x0160
3x0161
3x0162
3x0163 | Cool coil type | 0=None,1..8=N/A, 9..10=Water, 11..15=N/A | 0 | 15
3x0164 | Cool water temperature | Present cool water temperature for water cool coil. | -55.00 | 125.00 | °C
3x0165
3x0166
3x0167
3x0168 | Cool input level |  | 0.00 | 100.00 | %
3x0169 | Cool operation time | Total operation time of cool presented in days (24h). | 0 | 30000 | Days
3x0170
3x0171
3x0172
3x0173
Xzone temperature sensors
3x0174 | Xzone SA temperature | Present supply air temperature. | -55.00 | 125.00 | °C
3x0175 | Xzone EA temperature | Present extract air temperature in the unit. | -55.00 | 125.00 | °C
3x0176 | Xzone EA regulation temperature | Present extract air temperature used for regulation. | -55.00 | 125.00 | °C
3x0177 | Xzone Room temperature 1 | Present room temperature of sensor 1. | -55.00 | 125.00 | °C
3x0178 | Xzone Room temperature 2 | Present room temperature of sensor 2. | -55.00 | 125.00 | °C
3x0179 | Xzone Room temperature 3 | Present room temperature of sensor 3. | -55.00 | 125.00 | °C
3x0180 | Xzone Room temperature 4 | Present room temperature of sensor 4. | -55.00 | 125.00 | °C
3x0181 | Xzone Room temperature min/max/average | Present calculated min, max or average (depending on configuration) temperature of room sensor 1-4. | -55.00 | 125.00 | °C
3x0182
3x0183
3x0184
3x0185
Xzone Temperature regulation
3x0186 | Xzone SA Temp regulator | Present supply air temperature regulator set point. | 0.00 | 50.00 | °C
3x0187 | Xzone EA Temp regulator | Present extract air temperature regulator set point. | 0.00 | 50.00 | °C
3x0188
3x0189
3x0190 | Xzone re-heat regulator level |  | 0.00 | 100.00 | %
3x0191
3x0192
3x0193 | Xzone cool regulator level |  | 0.00 | 100.00 | %
3x0194
3x0195
3x0196
3x0197
Xzone coils
3x0198 | Xzone heat, coil type | 0=None,1..8=Electric, 9..10=Water, 11..15=Electric | 0 | 15
3x0199 | Xzone heat, anti frost temp/overheat input | Present Xzone heat anti frost temperature for water heat coil. Value 0=Overheat when electric heat is used. | -55.00 | 125.00 | °C
3x0200 | Xzone heat/cool temperature guard |  | 0.00 | 100.00 | °C |  | 2.47
3x0201
3x0202
3x0203 | Xzone heat, output level | Present level of Xzone heat output. | 0 | 100.00 | %
3x0204 | Xzone heat, input level | Present Xzone heat input. | 0 | 100.00 | %
3x0205 | Xzone heat, operation time | Total operation time of Xzone heat presented in days (24h). | 0 | 30000
3x0206
3x0207
3x0208
3x0209 | Xzone cool, coil type | 9..10=Water | 0 | 15
3x0210 | Xzone cool, water temperature |  | -55.00 | 125.00 | °C
3x0211 | Xzone cool temperature guard |  | 0.00 | 100.00 | °C |  | 2.47
3x0212
3x0213
3x0214 | Xzone cool, output level | Present level of Xzone cool. | 0 | 100.00 | %
3x0215 | Xzone cool, input level | Present Xzone cool valve position. | 0 | 100.00 | %
3x0216 | Xzone cool, operation time | Total operation time of Xzone cool presented in days (24h). | 0 | 30000
3x0217
3x0218
3x0219
Pre-heat
3x0220 | Pre-heat temperature | Present pre-heat temperature. | -55.00 | 125.00 | °C
3x0221 | Pre-heat temp regulator set point | Present pre-heat temperature regulator set point. | -40.00 | 40.00 | °C
3x0222 | Pre-heat temp regulator level
3x0223
3x0224 | Pre-heat coil type | 0=None,1..8=Electric, 9..10=Water, 11..15=Electric | 0 | 15
3x0225 | Pre-heat anti frost temp/overheat input | Present pre-heat anti frost temperature for water heat coil. Value 0=Overheat when electric heat is used. | -55.00 | 125.00 | °C
3x0226
3x0227
3x0228 | Pre-heat output level | Present pre-heat output level. | 0.00 | 100.00 | %
3x0229 | Pre-heat input level | Present pre-heat input level. | 0.00 | 100.00 | %
3x0230 | Pre-heat operation time | Total operation time of pre-heat presented in days (24h). | 0 | 30000 | Days
3x0231
3x0232
ReCO2
3x0233 | ReCO2 recirculation damper output | Present output signal to the recirculation damper. | 0.00 | 100.00 | %
3x0234 | ReCO2 recirculation damper input | Present input signal from the recirculation damper. | 0.00 | 100.00 | %
3x0235 | ReCO2 outdoor damper output | Present output signal to the outdoor air damper. | 0.00 | 100.00 | %
3x0236 | ReCO2 outdoor damper input | Present input signal from the outdoor air damper. | 0.00 | 100.00 | %
3x0237 | ReCO2 outdoor air flow | Present outdoor air flow level. | 0.0 | 3x0057 | l/s
3x0238 | ReCO2 outdoor air flow regulator set point | Present outdoor air flow regulator set point. | 0.0 | 3x0057 | l/s
3x0239
3x0240
3x0241
3x0242
3x0243
Humidity
3x0244 | SA humidity level | Present level of supply air humidity | 0.00 | 100.00 | %RH
3x0245 | SA humidity temperature | Present temperature inside the supply air humidity sensor. | -40.00 | 123.00 | °C
3x0246 | SA dew point | Calculated supply air dew point. | -40.00 | 40.00 | °C
3x0247 | EA humidity level | Present level of extract air humidity. | 0.00 | 100.00 | %RH
3x0248 | EA humidity temperature | Present temperature inside the extract air humidity sensor. | -40.00 | 123.00 | °C
3x0249 | EA dew point | Calculated extract air dew point. | -40.00 | 40.00 | °C
3x0250
3x0251 | Dehumidifying SA dew point regulator set point | Present supply air dew point regulator point. | -40.00 | 40.00 | °C
3x0252 | Dehumidifying output level | Present level of the dehumidifying output. | 0.00 | 100.00 | %
3x0253
3x0254 | Humidifying SA regulator set point |  | 0.00 | 100.00 | %RH
3x0255 | Humidifying output level | Present level of the humidifying output. | 0.00 | 100.00 | %
3x0256
3x0257
3x0258
3x0259
3x0260 | Exhaust air humidity | Present level of exhaust air humidity. | 0.00 | 100.00 | %RH |  | 1.23
3x0261 | Exhaust air temperature | Present temperature inside the exhaust air humidity sensor. | -40.00 | 123.00 | °C |  | 1.23
3x0262 | Outdoor air humidity | Present level of outdoor air humidity. | 0.00 | 100.00 | %RH |  | 2.37
3x0263 | Outdoor air temperature | Present temperature inside the outdoor air humidity sensor. | -40.00 | 123.00 | °C |  | 2.37
3x0264 | Room air humidity | Present level of room air humidity. | 0.00 | 100.00 | %RH |  | 2.37
3x0265 | Room air temperature | Present temperature inside the room air humidity sensor. | -40.00 | 123.00 | °C |  | 2.37
VOC
3x0266 | VOC level | Present level of VOC | 450 | 10000 | ppm
3x0267 | CO2 level | Present level of CO2 | 0 | 10000 | ppm |  | 1.23
3x0268
3x0269
3x0270
COOL DX
3x0271 | COOL DX, unit power size |  | 0 | 15
3x0272
3x0273
3x0274 | COOL DX, compressor 1 low pressure level |  | 0 | 34.50 | Bar
3x0275 | COOL DX, compressor 1 high pressure level |  | 0 | 45.00 | Bar
3x0276 | COOL DX, compressor 2 low pressure level |  | 0 | 34.50 | Bar
3x0277 | COOL DX, compressor 2 high pressure level |  | 0 | 45.00 | Bar
3x0278
3x0279
Exhaust heat
3x0280
3x0281 | Exhaust heat temperature | Present exhaust heat temperature | -55.00 | 125.00 | °C |  | 2.43
3x0282 | Exhaust heat temp regulator set point | Present exhaust heat temp regulator set point | -40.00 | 40.00 | °C |  | 2.43
3x0283 | Exhaust heat temp regulator level | [5 empty] | 2.43
3x0284 | Exhaust heat coil type | 0=None,1..8=Electric, 9..10=Water, 11..15=Electric | 0 | 15 |  |  | 2.43
3x0285 | Exhaust heat anti frost temp/overheat input | Present exhaust heat anti frost temperature for water heat coil. Value 0=Overheat when electric heat is used. | -55.00 | 125.00 | °C |  | 2.43
3x0286 | Exhaust heat output level | Present exhaust heat output level. | 0.00 | 100.00 | % |  | 2.43
3x0287 | Exhaust heat input level | Present exhaust heat input level. | 0.00 | 100.00 | % |  | 2.43
3x0288 | Exhaust heat operation time | Total operation time of exhaust heat presented in days (24h). | 0 | 30000 | Days |  | 2.43
SMART Link
3x0289 | SMART Link, WB outlet water 1 |  | -40.0 | 176.0 | °C
3x0290 | SMART Link, WB outlet water 2 |  | -40.0 | 176.0 | °C
3x0291 | SMART Link, WB outlet water 3 |  | -40.0 | 176.0 | °C
3x0292 | SMART Link, WB outlet water 4 |  | -40.0 | 176.0 | °C
3x0293 | SMART Link, WB outlet water average |  | -40.0 | 176.0 | °C
3x0294 | SMART Link, WB reference water
3x0295
3x0296
3x0297 | SMART Link WB, heated water set point |  | -40.0 | 176.0 | °C
3x0298 | SMART Link WB, chilled water set point |  | -40.0 | 176.0 | °C
3x0299 | SMART Link WB, Min heated water set point |  | -40.0 | 176.0 | °C
3x0300 | SMART Link WB, Max heated water set point |  | -40.0 | 176.0 | °C
3x0301 | SMART Link WB, Min chilled water set point |  | -40.0 | 176.0 | °C
3x0302 | SMART Link WB, Max chilled water set point |  | -40.0 | 176.0 | °C
3x0303
3x0304
3x0305
3x0306
3x0307
3x0308
3x0309
3x0310
3x0311
3x0312
3x0313
3x0314
3x0315
3x0316
3x0317
3x0318
3x0319 | SMART Link, WB operation
3x0320 | SMART Link, WB cool mode
3x0321
3x0322
3x0323 | SMART Link, DX unit 1 operation |  | 0 | 1
3x0324 | SMART Link, DX unit 1 cool mode |  | 0 | 1
3x0325 | SMART Link, DX unit 1 defrost request |  | 0 | 1
3x0326 | SMART Link, DX unit 1 defrost active |  | 0 | 1
3x0327 | SMART Link, DX unit 1 power level set point |  | 0 | 100.00 | %
3x0328 | SMART Link, DX unit 1 power level |  | 0 | 100.00 | %
3x0329 | SMART Link, DX unit 1 operation time |  | 0 | 9999
3x0330
3x0331
3x0332
3x0333
3x0334 | SMART Link, DX unit 2 operation |  | 0 | 1
3x0335 | SMART Link, DX unit 2 cool mode |  | 0 | 1
3x0336 | SMART Link, DX unit 2 defrost request |  | 0 | 1
3x0337 | SMART Link, DX unit 2 defrost active |  | 0 | 1
3x0338 | SMART Link, DX unit 2 power level set point |  | 0 | 100.00 | %
3x0339 | SMART Link, DX unit 2 power level |  | 0 | 100.00 | %
3x0340 | SMART Link, DX unit 2 operation time |  | 0 | 9999
3x0341
3x0342
3x0343
3x0344
3x0345 | SMART Link, DX unit 3 operation |  | 0 | 1
3x0346 | SMART Link, DX unit 3 cool mode |  | 0 | 1
3x0347 | SMART Link, DX unit 3 defrost request |  | 0 | 1
3x0348 | SMART Link, DX unit 3 defrost active |  | 0 | 1
3x0349 | SMART Link, DX unit 3 power level set point |  | 0 | 100.00 | %
3x0350 | SMART Link, DX unit 3 power level |  | 0 | 100.00 | %
3x0351 | SMART Link, DX unit 3 operation time |  | 0 | 9999
3x0352
3x0353
3x0354
3x0355
3x0356 | SMART Link, DX unit 4 operation |  | 0 | 1
3x0357 | SMART Link, DX unit 4 cool mode |  | 0 | 1
3x0358 | SMART Link, DX unit 4 defrost request |  | 0 | 1
3x0359 | SMART Link, DX unit 4 defrost active |  | 0 | 1
3x0360 | SMART Link, DX unit 4 power level set point |  | 0 | 100.00 | %
3x0361 | SMART Link, DX unit 4 power level |  | 0 | 100.00 | %
3x0362 | SMART Link, DX unit 4 operation time |  | 0 | 9999
3x0363
3x0364
3x0365
3x0366
3x0367 | SMART Link, DX Defrost airflow increase status |  | 0 | 1 |  |  | 1.26
3x0368
3x0369
3x0370
3x0371
3x0372
3x0373
AYC
3x0374 | AYC Heat, heated water | Present heat temperature. | -55.00 | 125.00 | °C
3x0375 | AYC Heat, heated water set point | Present heat temperature regulator set point. | 0 | 100.00 | °C
3x0376 | AYC Heat, valve output | Present level of the heat valve output. | 0 | 100.00 | %
3x0377 | AYC Heat, valve input | Present level of the heat valve input. | 0 | 100.00 | %
3x0378 | AYC Heat, operation time | Total operation time of AYC heat presented in days (24h). | 0 | 30000
3x0379 | AYC Heated water heat demand |  | 0 | 100.00 | % |  | 1.10
3x0380
3x0381
3x0382
3x0383
3x0384
3x0385
3x0386
3x0387 | AYC Cool, chilled water | Present cool temperature. | -55.00 | 125.00 | °C
3x0388 | AYC Cool, chilled water set point | Present cool temperature regulator set point. | 0 | 100.00 | °C
3x0389 | AYC Cool, valve output | Present cool of the heat valve output. | 0 | 100.00 | %
3x0390 | AYC Cool, valve input | Present cool of the heat valve input. | 0 | 100.00 | %
3x0391 | AYC Cool, operation time | Total operation time of AYC cool presented in days (24h). | 0 | 30000
3x0392 | AYC Chilled water cool demand |  | 0 | 100.00 | % |  | 1.10
3x0393
3x0394
3x0395
3x0396
3x0397
3x0398
3x0399
MIRU Control
3x0400 | MIRU Control 1 Min air flow | Min possible air flow setting |  |  | l/s
3x0401 | MIRU Control 1 Max air flow | Max possible air flow setting |  |  | l/s
3x0402 | MIRU Control 1 Air flow | Present air flow. |  |  | l/s
3x0403 | MIRU Control 1 Air flow set point | Present air flow regulator set point. |  |  | l/s
3x0404 | MIRU Control 1 Pressure | Present duct pressure. | 0 | 750 | Pa
3x0405 | MIRU Control 1 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
3x0406 | MIRU Control 1 External temperature | Present external temperature. | -55.00 | 95.00 | °C
3x0407 | MIRU Control 1 Operation time | Present operation time, present in days (24h). | 0 | 30000
3x0408 | MIRU Control 1 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
3x0409 | MIRU Control 1 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
3x0410 | MIRU Control 1 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
3x0411 | MIRU Control 1 kWh | kWh value. | 0 | 9999 | kWh
3x0412 | MIRU Control 1 MWh | MWh value. | 0 | 32000 | MWh
3x0413
3x0414
3x0415
3x0416
3x0417 | MIRU Control 2 Min air flow | Min possible air flow setting |  |  | l/s
3x0418 | MIRU Control 2 Max air flow | Max possible air flow setting |  |  | l/s
3x0419 | MIRU Control 2 Air flow | Present air flow. |  |  | l/s
3x0420 | MIRU Control 2 Air flow set point | Present air flow regulator set point. |  |  | l/s
3x0421 | MIRU Control 2 Pressure | Present duct pressure. | 0 | 750 | Pa
3x0422 | MIRU Control 2 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
3x0423 | MIRU Control 2 External temperature | Present external temperature. | -55.00 | 95.00 | °C
3x0424 | MIRU Control 2 Operation time | Present operation time, present in days (24h). | 0 | 30000
3x0425 | MIRU Control 2 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
3x0426 | MIRU Control 2 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
3x0427 | MIRU Control 2 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
3x0428 | MIRU Control 2 kWh | kWh value. | 0 | 9999 | kWh
3x0429 | MIRU Control 2 MWh | MWh value. | 0 | 32000 | MWh
3x0430
3x0431
3x0432
3x0433
3x0434 | MIRU Control 3 Min air flow | Min possible air flow setting |  |  | l/s
3x0435 | MIRU Control 3 Max air flow | Max possible air flow setting |  |  | l/s
3x0436 | MIRU Control 3 Air flow | Present air flow. |  |  | l/s
3x0437 | MIRU Control 3 Air flow set point | Present air flow regulator set point. |  |  | l/s
3x0438 | MIRU Control 3 Pressure | Present duct pressure. | 0 | 750 | Pa
3x0439 | MIRU Control 3 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
3x0440 | MIRU Control 3 External temperature | Present external temperature. | -55.00 | 95.00 | °C
3x0441 | MIRU Control 3 Operation time | Present operation time, present in days (24h). | 0 | 30000
3x0442 | MIRU Control 3 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
3x0443 | MIRU Control 3 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
3x0444 | MIRU Control 3 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
3x0445 | MIRU Control 3 kWh | kWh value. | 0 | 9999 | kWh
3x0446 | MIRU Control 3 MWh | MWh value. | 0 | 32000 | MWh
3x0447
3x0448
3x0449
3x0450
3x0451 | MIRU Control 4 Min air flow | Min possible air flow setting |  |  | l/s
3x0452 | MIRU Control 4 Max air flow | Max possible air flow setting |  |  | l/s
3x0453 | MIRU Control 4 Air flow | Present air flow. |  |  | l/s
3x0454 | MIRU Control 4 Air flow set point | Present air flow regulator set point. |  |  | l/s
3x0455 | MIRU Control 4 Pressure | Present duct pressure. | 0 | 750 | Pa
3x0456 | MIRU Control 4 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
3x0457 | MIRU Control 4 External temperature | Present external temperature. | -55.00 | 95.00 | °C
3x0458 | MIRU Control 4 Operation time | Present operation time, present in days (24h). | 0 | 30000
3x0459 | MIRU Control 4 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
3x0460 | MIRU Control 4 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
3x0461 | MIRU Control 4 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
3x0462 | MIRU Control 4 kWh | kWh value. | 0 | 9999 | kWh
3x0463 | MIRU Control 4 MWh | MWh value. | 0 | 32000 | MWh
3x0464
3x0465
3x0466
3x0467
3x0468 | MIRU Control 5 Min air flow | Min possible air flow setting |  |  | l/s
3x0469 | MIRU Control 5 Max air flow | Max possible air flow setting |  |  | l/s
3x0470 | MIRU Control 5 Air flow | Present air flow. |  |  | l/s
3x0471 | MIRU Control 5 Air flow set point | Present air flow regulator set point. |  |  | l/s
3x0472 | MIRU Control 5 Pressure | Present duct pressure. | 0 | 750 | Pa
3x0473 | MIRU Control 5 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
3x0474 | MIRU Control 5 External temperature | Present external temperature. | -55.00 | 95.00 | °C
3x0475 | MIRU Control 5 Operation time | Present operation time, present in days (24h). | 0 | 30000
3x0476 | MIRU Control 5 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
3x0477 | MIRU Control 5 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
3x0478 | MIRU Control 5 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
3x0479 | MIRU Control 5 kWh | kWh value. | 0 | 9999 | kWh
3x0480 | MIRU Control 5 MWh | MWh value. | 0 | 32000 | MWh
3x0481
3x0482
3x0483
3x0484
3x0485 | MIRU Control 6 Min air flow | Min possible air flow setting |  |  | l/s
3x0486 | MIRU Control 6 Max air flow | Max possible air flow setting |  |  | l/s
3x0487 | MIRU Control 6 Air flow | Present air flow. |  |  | l/s
3x0488 | MIRU Control 6 Air flow set point | Present air flow regulator set point. |  |  | l/s
3x0489 | MIRU Control 6 Pressure | Present duct pressure. | 0 | 750 | Pa
3x0490 | MIRU Control 6 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
3x0491 | MIRU Control 6 External temperature | Present external temperature. | -55.00 | 95.00 | °C
3x0492 | MIRU Control 6 Operation time | Present operation time, present in days (24h). | 0 | 30000
3x0493 | MIRU Control 6 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
3x0494 | MIRU Control 6 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
3x0495 | MIRU Control 6 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
3x0496 | MIRU Control 6 kWh | kWh value. | 0 | 9999 | kWh
3x0497 | MIRU Control 6 MWh | MWh value. | 0 | 32000 | MWh
3x0498
3x0499
3x0500
3x0501
3x0502 | MIRU Control 7 Min air flow | Min possible air flow setting |  |  | l/s
3x0503 | MIRU Control 7 Max air flow | Max possible air flow setting |  |  | l/s
3x0504 | MIRU Control 7 Air flow | Present air flow. |  |  | l/s
3x0505 | MIRU Control 7 Air flow set point | Present air flow regulator set point. |  |  | l/s
3x0506 | MIRU Control 7 Pressure | Present duct pressure. | 0 | 750 | Pa
3x0507 | MIRU Control 7 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
3x0508 | MIRU Control 7 External temperature | Present external temperature. | -55.00 | 95.00 | °C
3x0509 | MIRU Control 7 Operation time | Present operation time, present in days (24h). | 0 | 30000
3x0510 | MIRU Control 7 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
3x0511 | MIRU Control 7 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
3x0512 | MIRU Control 7 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
3x0513 | MIRU Control 7 kWh | kWh value. | 0 | 9999 | kWh
3x0514 | MIRU Control 7 MWh | MWh value. | 0 | 32000 | MWh
3x0515
3x0516
3x0517
3x0518
3x0519 | MIRU Control 8 Min air flow | Min possible air flow setting |  |  | l/s
3x0520 | MIRU Control 8 Max air flow | Max possible air flow setting |  |  | l/s
3x0521 | MIRU Control 8 Air flow | Present air flow. |  |  | l/s
3x0522 | MIRU Control 8 Air flow set point | Present air flow regulator set point. |  |  | l/s
3x0523 | MIRU Control 8 Pressure | Present duct pressure. | 0 | 750 | Pa
3x0524 | MIRU Control 8 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
3x0525 | MIRU Control 8 External temperature | Present external temperature. | -55.00 | 95.00 | °C
3x0526 | MIRU Control 8 Operation time | Present operation time, present in days (24h). | 0 | 30000
3x0527 | MIRU Control 8 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
3x0528 | MIRU Control 8 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
3x0529 | MIRU Control 8 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
3x0530 | MIRU Control 8 kWh | kWh value. | 0 | 9999 | kWh
3x0531 | MIRU Control 8 MWh | MWh value. | 0 | 32000 | MWh
3x0532
3x0533
3x0534
3x0535
3x0536 | MIRU Control 9 Min air flow | Min possible air flow setting |  |  | l/s
3x0537 | MIRU Control 9 Max air flow | Max possible air flow setting |  |  | l/s
3x0538 | MIRU Control 9 Air flow | Present air flow. |  |  | l/s
3x0539 | MIRU Control 9 Air flow set point | Present air flow regulator set point. |  |  | l/s
3x0540 | MIRU Control 9 Pressure | Present duct pressure. | 0 | 750 | Pa
3x0541 | MIRU Control 9 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
3x0542 | MIRU Control 9 External temperature | Present external temperature. | -55.00 | 95.00 | °C
3x0543 | MIRU Control 9 Operation time | Present operation time, present in days (24h). | 0 | 30000
3x0544 | MIRU Control 9 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
3x0545 | MIRU Control 9 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
3x0546 | MIRU Control 9 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
3x0547 | MIRU Control 9 kWh | kWh value. | 0 | 9999 | kWh
3x0548 | MIRU Control 9 MWh | MWh value. | 0 | 32000 | MWh
3x0549
3x0550
3x0551
3x0552
3x0553 | MIRU Control 10 Min air flow | Min possible air flow setting |  |  | l/s
3x0554 | MIRU Control 10 Max air flow | Max possible air flow setting |  |  | l/s
3x0555 | MIRU Control 10 Air flow | Present air flow. |  |  | l/s
3x0556 | MIRU Control 10 Air flow set point | Present air flow regulator set point. |  |  | l/s
3x0557 | MIRU Control 10 Pressure | Present duct pressure. | 0 | 750 | Pa
3x0558 | MIRU Control 10 Pressure set point | Present duct pressure regulator set point. | 0 | 750 | Pa
3x0559 | MIRU Control 10 External temperature | Present external temperature. | -55.00 | 95.00 | °C
3x0560 | MIRU Control 10 Operation time | Present operation time, present in days (24h). | 0 | 30000
3x0561 | MIRU Control 10 Fan level | Present running level of the fan. | 0.00 | 100.00 | %
3x0562 | MIRU Control 10 Fan power | Present power consumption level of the fan. | 0 | 6000 | W
3x0563 | MIRU Control 10 SFP | Present SFP value. | 0 | 5.00 | kW/m3/s
3x0564 | MIRU Control 10 kWh | kWh value. | 0 | 9999 | kWh
3x0565 | MIRU Control 10 MWh | MWh value. | 0 | 32000 | MWh
3x0566
3x0567
3x0568
3x0569
Software
3x0570 | IQlogic software version | Present controller software version | 0.00 | 99.00
3x0571
3x0572
3x0573
3x0574
3x0575
3x0576
3x0577
3x0578
3x0579
3x0580
3x0581
3x0582
3x0583
3x0584
3x0585
3x0586
3x0587
3x0588
3x0589
3x0590
3x0591 | AHU Version | 1=Version 1 2=Version 2 3=Version 3 4=Version 4 5=Version A 6=Version B 7=Version C 8=Version D 9=Version E 10=Version F |  |  |  |  | 2.44
Operation level
3x0592 | Operation level | 0=Fan not available 1=Alarm stop 2=Manual total stop (on hand terminal) 3=External total stop (digital input) 4=Communication total stop 5=Communication normal stop 6=Communication extended normal stop 7=Time channel total stop 8=Time channel normal stop 9=Time channel extended normal stop 10=Low speed=normal stop 11=SA Fan starting up 12=Fan regulation blocked 13=ReCO2 100% recirculation(1.11) 14=Morning boost stop(1.11) 15=Intermittent night heat stop(1.11) 16=After cooling electric heater 17=COOL DX switch off delay 18=Damper switch off delay 19=Manual low speed (on hand terminal) 20=External low speed (digital input) 21=Extended external low speed 22=Communication low speed 23=Time channel low speed 24=Morning boost low speed 25=Intermittent night heat low speed 26=Manual high speed (on hand terminal) 27=External high speed (digital input) 28=Extended external high speed 29=Communication high speed 30=Time channel high speed 31=Summer night cooling high speed 32=Filter calibration 33=RHX Defrost calibration 34=ReCO2 calibration 35=AHU start up 36=Re-heat ramp down 37=HX ramp down 38=Air adjustment 39=Fans in operation with active fire alarm 40=PX bypass damper adjustment(1.12) | 0 | 100 |  |  | 1.12
3x0593
3x0594
3x0595
3x0596
3x0597
3x0598
3x0599
3x0600
3x0601
3x0602
3x0603
Alarms
3x0604 | Triggered alarm #1 | ((Alarm group - 1) x 15) + alarm number in group=Triggered alarm number. Zero if no triggered alarm. | 0 | 1500
3x0605 | Triggered alarm #2 |  | 0 | 1500
3x0606 | Triggered alarm #3 |  | 0 | 1500
3x0607 | Triggered alarm #4 |  | 0 | 1500
3x0608 | Triggered alarm #5 |  | 0 | 1500
3x0609 | Triggered alarm #6 |  | 0 | 1500
3x0610 | Triggered alarm #7 |  | 0 | 1500
3x0611 | Triggered alarm #8 |  | 0 | 1500
3x0612 | Triggered alarm #9 |  | 0 | 1500
3x0613 | Triggered alarm #10 |  | 0 | 1500
3x0614 | Triggered alarm group #1 | Zero if no triggered alarm group. | 0 | 100
3x0615 | Triggered alarm group #2 |  | 0 | 100
3x0616 | Triggered alarm group #3 |  | 0 | 100
3x0617 | Triggered alarm group #4 |  | 0 | 100
3x0618 | Triggered alarm group #5 |  | 0 | 100
3x0619 | Triggered alarm group #6 |  | 0 | 100
3x0620 | Triggered alarm group #7 |  | 0 | 100
3x0621 | Triggered alarm group #8 |  | 0 | 100
3x0622 | Triggered alarm group #9 |  | 0 | 100
3x0623 | Triggered alarm group #10 |  | 0 | 100
3x0624
3x0625
3x0626
3x0627
3x0628
3x0629
3x0630
3x0631
3x0632
3x0633
3x0634
3x0635
3x0636
3x0637
3x0638
3x0639
3x0640
3x0641
3x0642
3x0643
3x0644
3x0645
3x0646
3x0647
3x0648
3x0649
3x0650
3x0651
3x0652
3x0653
Time schedule
3x0654 | Weekday | The internal clock present weekday | 1 | 7
3x0655 | Current action | 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop | 1 | 5
3x0656 | Effective period | 0=Inactive, 1=Active | 0 | 1
3x0657 | Exception schedule 1 | 0=Inactive, 1=Active | 0 | 1
3x0658 | Exception schedule 2 | 0=Inactive, 1=Active | 0 | 1
3x0659 | Calendar 1 | 0=Inactive, 1=Active | 0 | 1
3x0660 | Calendar 2 | 0=Inactive, 1=Active | 0 | 1
3x0661 | Prolonged low speed remaining hours | Prolonged external low speed remaining operation. | 0 | 23 |  |  | 1.13
3x0662 | Prolonged low speed remaining seconds | Prolonged external low speed remaining operation. | 0 | 3600 |  |  | 1.13
3x0663 | Prolonged high speed remaining hours | Prolonged external high speed remaining operation. | 0 | 23 |  |  | 1.13
3x0664 | Prolonged high speed remaining seconds | Prolonged external high speed remaining operation. | 0 | 3600 |  |  | 1.13
3x0665 | Schedule exception invalid data | 0=Inactive, 1=Active | 0 | 1 |  |  | 2.34
3x0666 | Calendar 1 invalid data | 0=Inactive, 1=Active | 0 | 1 |  |  | 2.34
3x0667 | Calendar 2 invalid data | 0=Inactive, 1=Active | 0 | 1 |  |  | 2.34
3x0668
3x0669
3x0670
3x0671
3x0672
3x0673
3x0674
3x0675
3x0676
3x0677
3x0678
3x0679
Reserved
3x0680
3x0681
3x0682
3x0683
3x0684
3x0685
3x0686
3x0687
3x0688
3x0689
3x0690
3x0691
3x0692
3x0693
3x0694
3x0695
3x0696
3x0697 | Exhaust heat heat retention at stop |  | 0.00 | 40.00 | °C |  | 2.43
3x0698 | Exhaust heat heat retention at operation |  | 0.00 | 40.00 | °C |  | 2.43
3x0699 | Exhaust heat frost protection alarm limit |  | 0.00 | 40.00 | °C |  | 2.43
3x0700 | Extra regulation sequence 2 heat regulator level | Present level of extra regulation heat. | 0.00 | 100.00 | % |  | 1.13
3x0701 | Extra regulation sequence 2 heat output level | Present level of extra regulation heat. | 0.00 | 100.00 | % |  | 1.13
3x0702 | Extra regulation sequence 2 cool regulator level | Present level of extra regulation cool. | 0.00 | 100.00 | % |  | 1.13
3x0703 | Extra regulation sequence 2 cool output level | Present level of extra regulation cool. | 0.00 | 100.00 | % |  | 1.13
3x0704 | Re-heat retention at stop |  | 0.00 | 40.00 | °C |  | 1.20
3x0705 | Re-heat retention at operation |  | 0.00 | 40.00 | °C |  | 1.20
3x0706 | Re-heat frost protection alarm limit |  | 0.00 | 40.00 | °C |  | 1.20
3x0707 | Pre-heat retention at stop |  | 0.00 | 40.00 | °C |  | 1.20
3x0708 | Pre-heat retention at operation |  | 0.00 | 40.00 | °C |  | 1.20
3x0709 | Pre-heat frost protection alarm limit |  | 0.00 | 40.00 | °C |  | 1.20
3x0710 | Xzone heat retention at stop |  | 0.00 | 40.00 | °C |  | 1.20
3x0711 | Xzone heat retention at operation |  | 0.00 | 40.00 | °C |  | 1.20
3x0712 | Xzone frost protection alarm limit |  | 0.00 | 40.00 | °C |  | 1.20
3x0713 | Extra regulation sequence 1 heat retention at stop |  | 0.00 | 40.00 | °C |  | 1.20
3x0714 | Extra regulation sequence 1 heat retention at operation |  | 0.00 | 40.00 | °C |  | 1.20
3x0715 | Extra regulation sequence 1 frost protection alarm limit |  | 0.00 | 40.00 | °C |  | 1.20
3x0716 | Extra regulation sequence 2 heat retention at stop |  | 0.00 | 40.00 | °C |  | 1.20
3x0717 | Extra regulation sequence 2 heat retention at operation |  | 0.00 | 40.00 | °C |  | 1.20
3x0718 | Extra regulation sequence 2 frost protection alarm limit |  | 0.00 | 40.00 | °C |  | 1.20
Energy monitoring
3x0719 | Heat exchange motor power consumption W |  | 0 | 10000 | W |  | 1.28
3x0720 | Heat exchange motor power consumption kW |  | 0.000 | 10.000 | kW |  | 1.28
3x0721 | Heat exchange motor energy consumption kWh |  | 0 | 999 | kWh |  | 1.28
3x0722 | Heat exchange motor energy consumption MWh |  | 0 | 30000 | MWh |  | 1.28
3x0723 | Heat power recovery W |  | -999 | 999 | W |  | 1.28
3x0724 | Heat power recovery kW |  | -30000 | 30000 | kW |  | 1.28
3x0725 | Heat power consumption W |  | -999 | 999 | W |  | 1.28
3x0726 | Heat power consumption kW |  | -30000 | 30000 | kW |  | 1.28
3x0727 | Cool power recovery W |  | -999 | 999 | W |  | 1.28
3x0728 | Cool power recovery kW |  | -30000 | 30000 | kW |  | 1.28
3x0729 | Cool power consumption W |  | -999 | 999 | W |  | 1.28
3x0730 | Cool power consumption kW |  | -30000 | 30000 | kW |  | 1.28
3x0731 | Heat energy recovery kWh |  | 0 | 999 | kWh |  | 1.28
3x0732 | Heat energy recovery MWh |  | 0 | 30000 | MWh |  | 1.28
3x0733 | Cool energy recovery kWh |  | 0 | 999 | kWh |  | 1.28
3x0734 | Cool energy recovery MWh |  | 0 | 30000 | MWh |  | 1.28
3x0735 | Heat energy consumption kWh |  | 0 | 999 | kWh |  | 1.28
3x0736 | Heat energy consumption MWh |  | 0 | 30000 | MWh |  | 1.28
3x0737 | Cool energy consumption kWh |  | 0 | 999 | kWh |  | 1.28
3x0738 | Cool energy consumption MWh |  | 0 | 30000 | MWh |  | 1.28
3x0739 | Pulse counter input 1 kWh |  | 0 | 999 | kWh |  | 2.36
3x0740 | Pulse counter input 1 MWh |  | 0 | 30000 | MWh |  | 2.36
3x0741 | Pulse counter input 2 kWh |  | 0 | 999 | kWh |  | 2.36
3x0742 | Pulse counter input 2 MWh |  | 0 | 30000 | MWh |  | 2.36
3x0743 | Pulse counter input 3 kWh |  | 0 | 999 | kWh |  | 2.36
3x0744 | Pulse counter input 3 MWh |  | 0 | 30000 | MWh |  | 2.36
3x0745 | Pulse counter input 4 kWh |  | 0 | 999 | kWh |  | 2.36
3x0746 | Pulse counter input 4 MWh |  | 0 | 30000 | MWh |  | 2.36
3x0747 | Re-heat water coil power consumption W |  | 0 | 999 | W |  | 2.47
3x0748 | Re-heat water coil power consumption kW |  | 0 | 30000 | kW |  | 2.47
3x0749 | Re-heat water coil energy consumption kWh |  | 0 | 999 | kWh |  | 2.47
3x0750 | Re-heat water coil energy consumption MWh |  | 0 | 30000 | MWh |  | 2.47
3x0751 | Cool water coil power consumption W |  | 0 | 999 | W |  | 2.47
3x0752 | Cool water coil power consumption kW |  | 0 | 30000 | kW |  | 2.47
3x0753 | Cool water coil energy consumption kWh |  | 0 | 999 | kWh |  | 2.47
3x0754 | Cool water coil energy consumption MWh |  | 0 | 30000 | MWh |  | 2.47
3x0755 | Xzone heat water coil power consumption W |  | 0 | 999 | W |  | 2.47
3x0756 | Xzone heat water coil power consumption kW |  | 0 | 30000 | kW |  | 2.47
3x0757 | Xzone heat water coil energy consumption kWh |  | 0 | 999 | kWh |  | 2.47
3x0758 | Xzone heat water coil energy consumption MWh |  | 0 | 30000 | MWh |  | 2.47
3x0759 | Xzone cool water coil power consumption W |  | 0 | 999 | W |  | 2.47
3x0760 | Xzone cool water coil power consumption kW |  | 0 | 30000 | kW |  | 2.47
3x0761 | Xzone cool water coil energy consumption kWh |  | 0 | 999 | kWh |  | 2.47
3x0762 | Xzone cool water coil energy consumption MWh |  | 0 | 30000 | MWh |  | 2.47
3x0763 | Re-heat liquid flow level |  | 0.000 | 10.000 | l/s |  | 2.47
3x0764 | Cool liquid flow level |  | 0.000 | 10.000 | l/s |  | 2.47
3x0765 | Xzone heat liquid flow level |  | 0.000 | 10.000 | l/s |  | 2.47
3x0766 | Xzone cool liquid flow level |  | 0.000 | 10.000 | l/s |  | 2.47
3x0767
3x0768
3x0769
3x0770
3x0771
3x0772
3x0773
3x0774
3x0775
3x0776
3x0777
3x0778
3x0779
3x0780 | Re-heat return water temperature |  | 0.00 | 100.00 | °C |  | 2.47
3x0781 | Re-heat flow water temperature |  | 0.00 | 100.00 | °C |  | 2.47
3x0782 | Cool return water temperature |  | 0.00 | 100.00 | °C |  | 2.47
3x0783 | Cool flow water temperature |  | 0.00 | 100.00 | °C |  | 2.47
3x0784 | Xzone heat return water temperature |  | 0.00 | 100.00 | °C |  | 2.47
3x0785 | Xzone heat flow water temperature |  | 0.00 | 100.00 | °C |  | 2.47
3x0786 | Xzone cool return water temperature |  | 0.00 | 100.00 | °C |  | 2.47
3x0787 | Xzone cool flow water temperature |  | 0.00 | 100.00 | °C |  | 2.47
BMS I/O-modules
3x0800 | External operation I/O-module 3, analogue input 1 |  | 0.00 | 100.00 | % |  | 1.20
3x0801 | External operation I/O-module 3, analogue input 2 |  | 0.00 | 100.00 | % |  | 1.20
3x0802
3x0803
3x0804 | External operation I/O-module 3, analogue output 1 |  | 0.00 | 100.00 | % |  | 1.20
3x0805 | External operation I/O-module 3, analogue output 2 |  | 0.00 | 100.00 | % |  | 1.20
3x0806 | External operation I/O-module 6, analogue input 1 |  | 0.00 | 100.00 | % |  | 1.20
3x0807 | External operation I/O-module 6, analogue input 2 |  | 0.00 | 100.00 | % |  | 1.20
3x0808
3x0809
3x0810 | External operation I/O-module 6, analogue output 1 |  | 0.00 | 100.00 | % |  | 1.20
3x0811 | External operation I/O-module 6, analogue output 2 |  | 0.00 | 100.00 | % |  | 1.20
3x0812 | External operation I/O-module A, analogue input |  | 0.00 | 100.00 | % |  | 1.20
3x0813 | External operation I/O-module A, temp sensor 1 |  | -55.00 | 125.00 | °C |  | 1.20
3x0814 | External operation I/O-module A, temp sensor 2 |  | -55.00 | 125.00 | °C |  | 1.20
3x0815 | External operation I/O-module B, analogue input |  | 0.00 | 100.00 | % |  | 1.20
3x0816 | External operation I/O-module B, temp sensor 1 |  | -55.00 | 125.00 | °C |  | 1.20
3x0817 | External operation I/O-module B, temp sensor 2 |  | -55.00 | 125.00 | °C |  | 1.20
3x0818 | External operation I/O-module C, analogue input |  | 0.00 | 100.00 | % |  | 1.20
3x0819 | External operation I/O-module C, temp sensor 1 |  | -55.00 | 125.00 | °C |  | 1.20
3x0820 | External operation I/O-module C, temp sensor 2 |  | -55.00 | 125.00 | °C |  | 1.20
Alarms
3x1001 | Alarm group 1 | Bit0=Alarm1 Bit1=Alarm2 Bit2=Alarm3 Bit3=Alarm4 Bit4=Alarm5 Bit5=Alarm6 Bit6=Alarm7 Bit7=Alarm8 Bit8=Alarm9 Bit9=Alarm10 Bit10=Alarm11 Bit11=Alarm12 Bit12=Alarm13 Bit13=Alarm14 Bit14=Alarm15 | 0 | 32767 |  |  | 1.10
3x1002 | Alarm group 2 |  | 0 | 32767 |  |  | 1.10
3x1003 | Alarm group 3 |  | 0 | 32767 |  |  | 1.10
3x1004 | Alarm group 4 |  | 0 | 32767 |  |  | 1.10
3x1005 | Alarm group 5 |  | 0 | 32767 |  |  | 1.10
3x1006 | Alarm group 6 |  | 0 | 32767 |  |  | 1.10
3x1007 | Alarm group 7 |  | 0 | 32767 |  |  | 1.10
3x1008 | Alarm group 8 |  | 0 | 32767 |  |  | 1.10
3x1009 | Alarm group 9 |  | 0 | 32767 |  |  | 1.10
3x1010 | Alarm group 10 |  | 0 | 32767 |  |  | 1.10
3x1011 | Alarm group 11 |  | 0 | 32767 |  |  | 1.10
3x1012 | Alarm group 12 |  | 0 | 32767 |  |  | 1.10
3x1013 | Alarm group 13 |  | 0 | 32767 |  |  | 1.10
3x1014 | Alarm group 14 |  | 0 | 32767 |  |  | 1.10
3x1015 | Alarm group 15 |  | 0 | 32767 |  |  | 1.10
3x1016 | Alarm group 16 |  | 0 | 32767 |  |  | 1.10
3x1017 | Alarm group 17 |  | 0 | 32767 |  |  | 1.10
3x1018 | Alarm group 18 |  | 0 | 32767 |  |  | 1.10
3x1019 | Alarm group 19 |  | 0 | 32767 |  |  | 1.10
3x1020 | Alarm group 20 |  | 0 | 32767 |  |  | 1.10
3x1021 | Alarm group 21 |  | 0 | 32767 |  |  | 1.10
3x1022 | Alarm group 22 |  | 0 | 32767 |  |  | 1.10
3x1023 | Alarm group 23 |  | 0 | 32767 |  |  | 1.10
3x1024 | Alarm group 24 |  | 0 | 32767 |  |  | 1.10
3x1025 | Alarm group 25 |  | 0 | 32767 |  |  | 1.10
3x1026 | Alarm group 26 |  | 0 | 32767 |  |  | 1.10
3x1027 | Alarm group 27 |  | 0 | 32767 |  |  | 1.10
3x1028 | Alarm group 28 |  | 0 | 32767 |  |  | 1.10
3x1029 | Alarm group 29 |  | 0 | 32767 |  |  | 1.10
3x1030 | Alarm group 30 |  | 0 | 32767 |  |  | 1.10
3x1031 | Alarm group 31 |  | 0 | 32767 |  |  | 1.10
3x1032 | Alarm group 32 |  | 0 | 32767 |  |  | 1.10
3x1033 | Alarm group 33 |  | 0 | 32767 |  |  | 1.10
3x1034 | Alarm group 34 |  | 0 | 32767 |  |  | 1.10
3x1035 | Alarm group 35 |  | 0 | 32767 |  |  | 1.10
3x1036 | Alarm group 36 |  | 0 | 32767 |  |  | 1.10
3x1037 | Alarm group 37 |  | 0 | 32767 |  |  | 1.10
3x1038 | Alarm group 38 |  | 0 | 32767 |  |  | 1.10
3x1039 | Alarm group 39 |  | 0 | 32767 |  |  | 1.10
3x1040 | Alarm group 40 |  | 0 | 32767 |  |  | 1.10
3x1041 | Alarm group 41 |  | 0 | 32767 |  |  | 1.10
3x1042 | Alarm group 42 |  | 0 | 32767 |  |  | 1.10
3x1043 | Alarm group 43 |  | 0 | 32767 |  |  | 1.10
3x1044 | Alarm group 44 |  | 0 | 32767 |  |  | 1.10
3x1045 | Alarm group 45 |  | 0 | 32767 |  |  | 1.10
3x1046 | Alarm group 46 |  | 0 | 32767 |  |  | 1.10
3x1047 | Alarm group 47 |  | 0 | 32767 |  |  | 1.10
3x1048 | Alarm group 48 |  | 0 | 32767 |  |  | 1.10
3x1049 | Alarm group 49 |  | 0 | 32767 |  |  | 1.10
3x1050 | Alarm group 50 |  | 0 | 32767 |  |  | 1.10
3x1051 | Alarm group 51 |  | 0 | 32767 |  |  | 1.10
3x1052 | Alarm group 52 |  | 0 | 32767 |  |  | 1.10
3x1053 | Alarm group 53 |  | 0 | 32767 |  |  | 1.10
3x1054 | Alarm group 54 |  | 0 | 32767 |  |  | 1.10
3x1055 | Alarm group 55 |  | 0 | 32767 |  |  | 1.10
3x1056 | Alarm group 56 |  | 0 | 32767 |  |  | 1.10
3x1057 | Alarm group 57 |  | 0 | 32767 |  |  | 1.10
3x1058 | Alarm group 58 |  | 0 | 32767 |  |  | 1.10
3x1059 | Alarm group 59 |  | 0 | 32767 |  |  | 1.10
3x1060 | Alarm group 60 |  | 0 | 32767 |  |  | 1.10
3x1061 | Alarm group 61 |  | 0 | 32767 |  |  | 1.10
3x1062 | Alarm group 62 |  | 0 | 32767 |  |  | 1.10
3x1063 | Alarm group 63 |  | 0 | 32767 |  |  | 1.10
3x1064 | Alarm group 64 |  | 0 | 32767 |  |  | 1.10
3x1065 | Alarm group 65 |  | 0 | 32767 |  |  | 1.10
3x1066 | Alarm group 66 |  | 0 | 32767 |  |  | 1.10
3x1067 | Alarm group 67 |  | 0 | 32767 |  |  | 1.10
3x1068 | Alarm group 68 |  | 0 | 32767 |  |  | 1.10
3x1069 | Alarm group 69 |  | 0 | 32767 |  |  | 1.10
3x1070 | Alarm group 70 |  | 0 | 32767 |  |  | 1.10
3x1071 | Alarm group 71 |  | 0 | 32767 |  |  | 1.10
3x1072 | Alarm group 72 |  | 0 | 32767 |  |  | 1.10
3x1073 | Alarm group 73 |  | 0 | 32767 |  |  | 1.10
3x1074 | Alarm group 74 |  | 0 | 32767 |  |  | 1.10
3x1075 | Alarm group 75 |  | 0 | 32767 |  |  | 1.10
3x1076 | Alarm group 76 |  | 0 | 32767 |  |  | 1.10
3x1077 | Alarm group 77 |  | 0 | 32767 |  |  | 1.10
3x1078 | Alarm group 78 |  | 0 | 32767 |  |  | 1.10
3x1079 | Alarm group 79 |  | 0 | 32767 |  |  | 1.10
3x1080 | Alarm group 80 |  | 0 | 32767 |  |  | 1.10
3x1081 | Alarm group 81 |  | 0 | 32767 |  |  | 1.10
3x1082 | Alarm group 82 |  | 0 | 32767 |  |  | 1.10
3x1083 | Alarm group 83 |  | 0 | 32767 |  |  | 1.10
3x1084 | Alarm group 84 |  | 0 | 32767 |  |  | 1.10
3x1085 | Alarm group 85 |  | 0 | 32767 |  |  | 1.10
3x1086 | Alarm group 86 |  | 0 | 32767 |  |  | 1.10
3x1087 | Alarm group 87 |  | 0 | 32767 |  |  | 1.10
3x1088 | Alarm group 88 |  | 0 | 32767 |  |  | 1.10
3x1089 | Alarm group 89 |  | 0 | 32767 |  |  | 1.10
3x1090 | Alarm group 90 |  | 0 | 32767 |  |  | 1.10
3x1091 | Alarm group 91 |  | 0 | 32767 |  |  | 1.10
3x1092 | Alarm group 92 |  | 0 | 32767 |  |  | 1.10
3x1093 | Alarm group 93 |  | 0 | 32767 |  |  | 1.10
3x1094 | Alarm group 94 |  | 0 | 32767 |  |  | 1.10
3x1095 | Alarm group 95 |  | 0 | 32767 |  |  | 1.10
3x1096 | Alarm group 96 |  | 0 | 32767 |  |  | 1.10
3x1097 | Alarm group 97 |  | 0 | 32767 |  |  | 1.10
3x1098 | Alarm group 98 |  | 0 | 32767 |  |  | 1.10
3x1099 | Alarm group 99 |  | 0 | 32767 |  |  | 1.10
3x1100 | Alarm group 100 |  | 0 | 32767 |  |  | 1.10
H/C
3x1400 | H/C mode | 0=Inactive, 1=Active | 0 | 1 |  |  | 1.23
3x1401 | H/C defrost accessory | 0=Inactive, 1=Recirculation, 2=Electric heat | 0 | 2 |  |  | 1.23
3x1402 | H/C recirculation defrost active | 0=Inactive, 1=Active | 0 | 1 |  |  | 1.31
3x1403 | H/C defrost active | 0=Inactive, 1=Active | 0 | 1 |  |  | 1.31
3x1404
3x1405 | H/C recirculation defrost damper output |  | 0.00 | 100.00 | % |  | 1.23
3x1406 | H/C recirculation defrost damper input |  | 0.00 | 100.00 | % |  | 1.23
3x1407 | H/C heat type | 0=None,1..8=Electric, 9..10=Water, 11..15=Electric | 0 | 15 |  |  | 1.23
3x1408
3x1409 | H/C heat anti frost temp/overheat input | Present H/C heat anti frost temperature for water heat coil. Value 0=overheat when electric heat is used. | -55.00 | 125.00 | °C |  | 1.23
3x1410 | H/C operation mode | 0=Inactive, 1=Stop, 2=Stabilization, 3=Normal operation, 4=Comfort operation, 5=Economy operation, 6=Defrost, 7=Defrost, 8=Oil recovery | 0 | 8 |  |  | 1.23
3x1411 | H/C defrost mode | 0=Inactive, 1=Start delay, 2=Initializing, 3=Pre-defrosting, 4=Defrosting, 5=Draining | 0 | 5 |  |  | 1.23
3x1412 | H/C heat/cool mode | 0=Heating, 1=Cooling | 0 | 1 |  |  | 1.23
3x1413 | H/C operation level |  | 0.00 | 100.00 | % |  | 1.23
3x1414 | H/C heat defrost level |  | 0.00 | 100.00 | % |  | 1.23
3x1415 | H/C defrost pressure level |  | -500.0 | 2500.0 | Pa |  | 1.23
3x1416 | H/C defrost pressure start limit |  | 0.0 | 1000.0 | Pa |  | 1.23
3x1417 | H/C defrost pressure end limit |  | 0.0 | 1000.0 | Pa |  | 1.23
3x1418 | H/C superheat temp |  | 0.0 | 99.0 | K |  | 1.23
3x1419 | H/C discharge temp |  | -10.0 | 130.0 | °C |  | 1.23
3x1420 | H/C suction temp |  | -40.0 | 105.0 | °C |  | 1.23
3x1421 | H/C condensation temp |  | 0.0 | 1000.0 | °C |  | 1.23
3x1422 | H/C evaporation temp |  | 0.0 | 1000.0 | °C |  | 1.23
3x1423 | H/C high pressure |  | 0.10 | 50.00 | Bar |  | 1.23
3x1424 | H/C low pressure |  | 0.10 | 50.00 | Bar |  | 1.23

## Holding Registers
GOLD_E_F_Modbus_260227
Holding Registers. 16-bit integer value (R/W).
Modbus | Name | Description | Min | Max | Unit | Default | Misc
AHU fan regulation
4x0001 | SA Fan regulation mode | Setting of regulation type for the supply air fan. 0=Air flow reg. 1=Pressure reg. 2=Demand reg. 3=Slave controlled by EA fan | 0 | 3 |  | 0
4x0002 | EA Fan regulation mode | Setting of regulation type for the extract air fan. 0=Air flow reg. 1=Pressure reg. 2=Demand reg. 3=Slave controlled by SA fan | 0 | 3 |  | 0
Air flow regulation
4x0003 | SA low speed air flow set point | Supply air flow set point for the unit when running in low speed operation. | 0 | 4x0005 | l/s
4x0004 | EA low speed air flow set point | Extract air flow set point for the unit when running in low speed operation. | 0 | 4x0006 | l/s
4x0005 | SA high speed air flow set point | Supply air flow set point for the unit when running in high speed operation. | 4x0003 | 4x0007 | l/s
4x0006 | EA high speed air flow set point | Extract air flow set point for the unit when running in high speed operation. | 4x0004 | 4x0008 | l/s
4x0007 | SA max speed air flow set point bost | Supply air flow max. limit for the unit when the low/high speed operation set point is altered by boosting function etc. | 4x0005 | 3x0057 | l/s
4x0008 | EA max speed air flow set point bost | Extract air flow max. limit for the unit when the low/high speed operation set point is altered by boosting function etc. | 4x0006 | 3x0058 | l/s
4x0009 | SA regulation zone | Supply air flow regulation zone setting in % of the present air flow set point that the regulator is allowed to work within. | 1.00 | 10.00 | % | 7.50
4x0010 | EA regulation zone | Extract air flow regulation zone setting in % of the present air flow set point that the regulator is allowed to work within. | 1.00 | 10.00 | % | 7.50
4x0011 | SA regulation I-time | Supply air flow regulator affection setting. | 1 | 1800 | s | 30
4x0012 | EA regulation I-time | Extract air flow regulator affection setting. | 1 | 1800 | s | 30
4x0013
4x0014
4x0015
4x0016
4x0017
4x0018
Pressure regulation
4x0019 | SA low speed pressure set point | Supply air duct pressure set point for the unit when running in low speed operation. | 0.0 | 4x0021 | Pa
4x0020 | EA low speed pressure set point | Extract air duct pressure set point for the unit when running in low speed operation. | 0.0 | 4x0022 | Pa
4x0021 | SA high speed pressure set point | Supply air duct pressure for the unit when running in high speed operation. | 4x0019 | 4x0023 | Pa
4x0022 | EA high speed pressure set point | Extract air duct pressure set point for the unit when running in high speed operation. | 4x0020 | 4x0024 | Pa
4x0023 | SA max speed pressure set point | Supply air duct pressure max. limit for the unit when the low/high speed operation set point is altered by boosting function etc. | 4x0021 | 750.0 | Pa
4x0024 | EA max speed pressure set point | Extract air duct pressure max. limit for the unit when the low/high speed operation set point is altered by boosting function etc. | 4x0022 | 750.0 | Pa
4x0025 | SA max speed output signal | Max. limit for the supply air fan speed when running in pressure regulation mode. | 0 | 100.00 | %
4x0026 | EA max speed output signal | Max. limit for the extract air fan speed when running in pressure regulation mode. | 0 | 100.00 | %
4x0027 | SA pressure regulation zone | Supply air pressure regulation zone setting in % of the present duct pressure set point that the regulator is allowed to work within. | 1 | 40.00 | % | 15
4x0028 | EA pressure regulation zone | Extract air pressure regulation zone setting in % of the present duct pressure set point that the regulator is allowed to work within. | 1 | 40.00 | % | 15
4x0029 | SA pressure I-time | Supply air pressure regulator affection setting. | 0 | 1800 | s | 30
4x0030 | EA pressure I-time | Extract air pressure regulator affection setting. | 0 | 1800 | s | 30
4x0031
4x0032
Demand regulation
4x0033 | Demand low speed CO2 set point | Set point for the CO2 input signal for the unit when running in low speed operation. | 0 | 10000 | ppm | 1000 | 1.23
4x0034 | Demand high speed CO2 set point | Set point for the CO2 input signal for the unit when running in high speed operation. | 0 | 10000 | ppm | 750 | 1.23
4x0035 | Demand low speed VOC set point | Set point for the VOC input signal for the unit when running in low speed operation. | 0 | 10000 | ppm | 2500 | 1.23
4x0036 | Demand high speed VOC set point | Set point for the VOC input signal for the unit when running in high speed operation. | 0 | 10000 | ppm | 1500 | 1.23
4x0037 | Demand low speed set point | Set point for the 0..10V input signal for the unit when running in low speed operation. | 0.00 | 100.00 | % | 50.00 | 1.23
4x0038 | Demand high speed set point | Set point for the 0..10V input signal for the unit when running in high speed operation. | 10.00 | 100.00 | % | 25.00 | 1.23
4x0039 | SA min speed air flow set point | Supply air flow min. limit for the unit when the low/high speed operation set point is altered when running in fan regulation mode demand. | 3x0055 | 4x0041 | l/s
4x0040 | EA min speed air flow set point | Extract air flow min. limit for the unit when the low/high speed operation set point is altered when running in fan regulation mode demand. | 3x0056 | 4x0042 | l/s
4x0041 | SA max speed air flow set point demand | Supply air flow max limit for the unit when the low/high speed operation set point is altered when running in fan regulation mode demand. | 4x0039 | 3x0057 | l/s
4x0042 | EA max speed air flow set point demand | Extract air flow max. limit for the unit when the low/high speed operation set point is altered when running in fan regulation mode demand. | 4x0040 | 3x0058 | l/s
4x0043 | Demand P-band | Demand regulator P-band setting. | 1.00 | 100.00 | % | 40.00 | 1.23
4x0044 | Demand I-time | Demand regulator affection setting. | 1 | 1800 | s | 1200 | 1.23
4x0045 | Demand CO2 P-band | Demand C02 regulator P-band setting. | 0 | 10000 | ppm | 600 | 1.23
4x0046 | Demand VOC P-band | Demand VOC regulator P-band setting. | 0 | 10000 | ppm | 1000 | 1.23
4x0047
4x0048
4x0049
Slave controlled regulation
4x0050 | Slave offset factor |  | 50.00 | 200.00 | % | 0.00
4x0051 | SA slave offset air flow |  | - 4x0057 | 4x0057 | l/s | 0 | 1.31
4x0052 | EA slave offset air flow |  | - 4x0058 | 4x0058 | l/s | 0 | 1.31
Fans OA temp compensation
4x0053 | Outdoor temp compensation function | 0=Inactive, 1=Active at low speed, 2=Active at high speed, 3=Active at low and high speed. | 0 | 3 |  | 0
4x0054 | Outdoor temp compensation X1 |  | -50.00 | 4x0055 | °C | -20.00
4x0055 | Outdoor temp compensation X2 |  | 4x0054 | 4x0056 | °C | -10.00
4x0056 | Outdoor temp compensation X3 |  | 4x0055 | 4x0057 | °C | 10.00
4x0057 | Outdoor temp compensation X4 |  | 4x0056 | 50.00 | °C | 20.00
4x0058 | Outdoor temp compensation Y1 SA air flow |  | 3x0055 | 3x0057 | l/s
4x0059 | Outdoor temp compensation Y2 SA air flow |  | 3x0055 | 3x0057 | l/s
4x0060 | Outdoor temp compensation Y3 SA air flow |  | 3x0055 | 3x0057 | l/s
4x0061 | Outdoor temp compensation Y4 SA air flow |  | 3x0055 | 3x0057 | l/s
4x0062 | Outdoor temp compensation Y1 EA air flow |  | 3x0056 | 3x0058 | l/s
4x0063 | Outdoor temp compensation Y2 EA air flow |  | 3x0056 | 3x0058 | l/s
4x0064 | Outdoor temp compensation Y3 EA air flow |  | 3x0056 | 3x0058 | l/s
4x0065 | Outdoor temp compensation Y4 EA air flow |  | 3x0056 | 3x0058 | l/s
4x0066 | Outdoor temp compensation Y1 SA pressure |  | 20.0 | 750.0 | Pa | 100.0
4x0067 | Outdoor temp compensation Y2 SA pressure |  | 20.0 | 750.0 | Pa | 100.0
4x0068 | Outdoor temp compensation Y3 SA pressure |  | 20.0 | 750.0 | Pa | 100.0
4x0069 | Outdoor temp compensation Y4 SA pressure |  | 20.0 | 750.0 | Pa | 100.0
4x0070 | Outdoor temp compensation Y1 EA pressure |  | 20.0 | 750.0 | Pa | 100.0
4x0071 | Outdoor temp compensation Y2 EA pressure |  | 20.0 | 750.0 | Pa | 100.0
4x0072 | Outdoor temp compensation Y3 EA pressure |  | 20.0 | 750.0 | Pa | 100.0
4x0073 | Outdoor temp compensation Y4 EA pressure |  | 20.0 | 750.0 | Pa | 100.0
4x0074
4x0075
4x0076
4x0077
Fans down regulation
4x0078 | Down regulation function | 0=Inactive, 1=SA, 2=SA and EA | 0 | 2 |  | 1
4x0079 | Down regulation neutral zone |  | 0.00 | 10.00 | K | 0.00
4x0080 | Down regulation P-band |  | 1.00 | 10.00 | K | 5.00
4x0081 | Down regulation I-time |  | 1 | 1800 | s | 30
4x0082
4x0083
Fans in operation at active fire alarm
4x0084 | Fans in operation at fire alarm 1 function | 0=Inactive, 1=SA, 2=EA, 3=SA and EA | 0 | 3
4x0085 | SA fan speed at fire alarm 1 |  | 0.00 | 100.00 | % | 100.00
4x0086 | EA fan speed at fire alarm 1 |  | 0.00 | 100.00 | % | 100.00
4x0087 | Fans in operation at fire alarm 2 function | 0=Inactive, 1=SA, 2=EA, 3=SA and EA | 0 | 3 |  |  | 1.10
4x0088 | SA fan speed at fire alarm 2 |  | 10.00 | 100.00 | % | 100.00 | 1.10
4x0089 | EA fan speed at fire alarm 2 |  | 10.00 | 100.00 | % | 100.00 | 1.10
4x0090 | Fans in operation at internal fire alarm function | 0=Inactive, 1=SA, 2=EA, 3=SA and EA | 0 | 3 |  |  | 1.10
4x0091 | SA fan speed at internal fire alarm |  | 10.00 | 100.00 | % | 100.00 | 1.10
4x0092 | EA fan speed at internal fire alarm |  | 10.00 | 100.00 | % | 100.00 | 1.10
4x0093
4x0094
Filters
4x0095 | Pre-filter function | 0=Inactive, 1=SA, 2=EA, 3=SA and EA | 0 | 3 |  | 0
4x0096 | Pre-filter calibration | 0=Inactive, 1=SA, 2=EA, 3=SA and EA | 0 | 3 |  | 0
4x0097 | SA pre-filter alarm limit |  | 30.0 | 500.0 | Pa | 100.0
4x0098 | EA pre-filter alarm limit |  | 30.0 | 500.0 | Pa | 100.0
4x0099
4x0100
4x0101 | AHU filter function | 0=Inactive, 1=SA, 2=EA, 3=SA and EA | 0 | 3
4x0102 | AHU filter calibration | 0=Inactive, 1=SA, 2=EA, 3=SA and EA | 0 | 3 |  | 0
4x0103 | SA AHU-filter alarm limit |  | 30.0 | 500.0 | Pa | 100.0
4x0104 | EA AHU-filter alarm limit |  | 30.0 | 500.0 | Pa | 100.0
4x0105
4x0106
4x0107 | SA end filter function | 0=Inactive, 1=SA | 0 | 1
4x0108 | SA end filter calibration | 0=Inactive, 1=SA | 0 | 1
4x0109 | SA end-filter alarm limit |  | 30.0 | 500.0 | Pa | 100.0
4x0110
Seasonal controlled temperature regulation
4x0111 | Seasonal controlled temperature regulation | 0=Inactive, 1=Active | 0 | 1 |  | 0 | 1.23
4x0112 | Seasonal controlled temperature regulation mode | 0=ERS-1, 1=ERS-2, 2=SA, 3=EA, 4=ORS, 5=ORE | 0 | 5 |  | 3 | 1.23
4x0113 | Seasonal controlled temperature regulation active |  | -20.00 | 40.00 | °C | 0.00 | 1.23
4x0114 | Seasonal controlled temperature regulation inactive |  | -20.00 | 40.00 | °C | 20.00 | 1.23
AHU Temperature regulation
4x0115 | Temperature regulation mode | 1=ERS-1, 2=ERS-2, 3=SA, 4=EA, 5=ORS, 6=ORE | 1 | 6 |  | 3
4x0116
ERS-1 reg.
4x0117 | ERS 1 step | Curve setting according to the diagram for ERS 1. | 1 | 4 |  | 2
4x0118 | ERS 1 diff | Supply air temp difference setting according to the diagram for ERS 1. | 1.00 | 7.00 | K | 2.00
4x0119 | ERS 1 breakpoint | Breakpoint temp setting according to the diagram for ERS 1. | 12.00 | 26.00 | °C | 22.00
4x0120
4x0121
ERS-2 reg.
4x0122 | ERS 2 breakpoint X1 | Breakpoint X1 setting according to the diagram for ERS 2. | 10.00 | 4x0123 | °C | 15.00
4x0123 | ERS 2 breakpoint X2 | Breakpoint X2 setting according to the diagram for ERS 2. | 4x0122 | 4x0124 | °C | 20.00
4x0124 | ERS 2 breakpoint X3 | Breakpoint X3 setting according to the diagram for ERS 2. | 4x0123 | 4x0125 | °C | 22.00
4x0125 | ERS 2 breakpoint X4 | Breakpoint X4 setting according to the diagram for ERS 2. | 4x0124 | 40.00 | °C | 24.00
4x0126 | ERS 2 breakpoint Y1 | Breakpoint Y1 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 20.00
4x0127 | ERS 2 breakpoint Y2 | Breakpoint Y2 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 18.00
4x0128 | ERS 2 breakpoint Y3 | Breakpoint Y3 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 14.00
4x0129 | ERS 2 breakpoint Y4 | Breakpoint Y4 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 12.00
4x0130
4x0131
SA Reg.
4x0132 | SA temperature set point | Supply air temperature setting, for supply air temp regulation mode. | 10.00 | 40.00 | °C | 21.00
4x0133
4x0134
EA Reg.
4x0135 | EA/Room temperature set point | Extract air/room temperature setting, for Extract air/room temp regulation mode. | 10.00 | 40.00 | °C | 21.00
4x0136 | SA min temp set point | Supply air min. set point during EA/room regulation mode. | 8.00 | 30.00 | °C | 16.00
4x0137 | SA max temp set point | Supply air max. set point during EA/room regulation mode. | 8.00 | 50.00 | °C | 28.00 | 1.18
4x0138 | EA regultaion P-band |  | 1.00 | 10.00 | K | 5.00
4x0139 | EA regultaion I-time |  | 1 | 1800 | s | 30
4x0140
4x0141
ORS Reg.
4x0142 | ORS breakpoint X1 | Breakpoint X1 setting according to the diagram for ORS. | -5.00 | 4x0143 | °C | -20.00
4x0143 | ORS breakpoint X2 | Breakpoint X2 setting according to the diagram for ORS. | 4x0142 | 4x0144 | °C | -10.00
4x0144 | ORS breakpoint X3 | Breakpoint X3 setting according to the diagram for ORS. | 4x0143 | 4x0145 | °C | 10.00
4x0145 | ORS breakpoint X4 | Breakpoint X4 setting according to the diagram for ORS. | 4x0144 | 50.00 | °C | 20.00
4x0146 | ORS breakpoint Y1 | Breakpoint Y1 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
4x0147 | ORS breakpoint Y2 | Breakpoint Y2 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
4x0148 | ORS breakpoint Y3 | Breakpoint Y3 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
4x0149 | ORS breakpoint Y4 | Breakpoint Y4 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
4x0150
4x0151
ORE Reg.
4x0152 | ORE breakpoint X1 | Breakpoint X1 setting according to the diagram for ORE. | -5.00 | 4x0153 | °C | -20.00
4x0153 | ORE breakpoint X2 | Breakpoint X2 setting according to the diagram for ORE. | 4x0152 | 4x0154 | °C | -10.00
4x0154 | ORE breakpoint X3 | Breakpoint X3 setting according to the diagram for ORE. | 4x0153 | 4x0155 | °C | 10.00
4x0155 | ORE breakpoint X4 | Breakpoint X4 setting according to the diagram for ORE. | 4x0154 | 50.00 | °C | 20.00
4x0156 | ORE breakpoint Y1 | Breakpoint Y1 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
4x0157 | ORE breakpoint Y2 | Breakpoint Y2 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
4x0158 | ORE breakpoint Y3 | Breakpoint Y3 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
4x0159 | ORE breakpoint Y4 | Breakpoint Y4 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
4x0160
4x0161
AHU external sensors
4x0162 | External room sensor 1 function |  | 0 | 1 |  | 0
4x0163 | External room sensor 2 function |  | 0 | 1 |  | 0
4x0164 | External room sensor 3 function |  | 0 | 1 |  | 0
4x0165 | External room sensor 4 function |  | 0 | 1 |  | 0
4x0166 | External room sensors measurement function | 0=Average, 1=Min, 2=Max | 0 | 2 |  | 0
4x0167 | External room temp from BMS function |  | 0 | 1 |  | 0
4x0168 | External room temp from BMS |  | -55.00 | 125.00 | °C | 0.00
4x0169 | External room temp from BMS alarm time |  | 0 | 9999 | min | 5
4x0170
4x0171
4x0172 | External OA sensor 1 function |  | 0 | 1 |  | 0
4x0173 | External OA sensor 2 function |  | 0 | 1 |  | 0
4x0174 | External OA sensor 3 function |  | 0 | 1 |  | 0
4x0175 | External OA sensor 4 function |  | 0 | 1 |  | 0
4x0176 | External OA sensors measurement function | 0=Average, 1=Min, 2=Max | 0 | 2 |  | 0
4x0177 | External OA temp from BMS function |  | 0 | 1 |  | 0
4x0178 | External OA temp from BMS |  | -55.00 | 125.00 | °C | 0.00
4x0179 | External OA temp from BMS alarm time |  | 0 | 9999 | min | 5
4x0180
4x0181
AHU Heat exchange
4x0182 | RHX defrost function | Setting for activating the defrost function for the rotary heat exchanger. | 0 | 1 |  | 0
4x0183 | RHX defrost calibration |  | 0 | 1 |  | 0
4x0184 | RHX defrost start limit |  | 30.0 | 100.0 | Pa | 50.0
4x0185
4x0186
4x0187 | RHX carry over control function | Setting for activating the carry over control function for the rotary heat exchanger. | 0 | 1 |  | 0
4x0188 | RHX sorption rotor function | Setting for activating the sorption rotor control function for the rotary heat exchanger. 0=inactive, 1=sorption max speed at cool recovery, 2=always sorption max speed. | 0 | 2 |  | 0 | 1.11
4x0189 | Rotor type | 0=RECOnomic, 1=STE, 2=MPE, 3=MTE | 0 | 3 |  | 0 | 2.36
4x0190 | RHX min exhaust air temp function |  | 0 | 1 |  | 0
4x0191 | RHX min exhaust air temp set point |  | -40.00 | 20.00 | °C | 5.00
4x0192 | RHX min exhaust air temp P-band |  | 1.00 | 40.00 | K | 8.00
4x0193 | RHX min exhaust air temp I-time |  | 0 | 30000 | s | 30
4x0194
4x0195
4x0196
4x0197
4x0198 | PHX periodic operation of bypass damper function |  | 0 | 1 |  | 1
4x0199 | PHX periodic operation interval |  | 0 | 168 | h | 24
4x0200 | PHX periodic operation time |  | 0 | 60 | min | 3
4x0201 | PHX Bypass optimize |  | 0 | 1 |  | 0 | 1.12
4x0202 | PHX supply air temp set point displacement |  | 0.00 | 10.00 | K | 0.00 | 2.48
4x0203
4x0204
4x0205 | CHX periodic operation of pump function |  | 0 | 1 |  | 1
4x0206 | CHX periodic operation of valve function |  | 0 | 1 |  | 1
4x0207 | CHX periodic operation interval |  | 0 | 168 | h | 24
4x0208 | CHX periodic operation time |  | 0 | 60 | min | 3
4x0209
4x0210
4x0211
4x0212
4x0213 | PHX/CHX Bypass defrost limit | PHX is default 3°C, CHX is default 5°C. | -10.00 | 5.00 | °C
4x0214 | PHX/CHX Bypass defrost P-band |  | 1.00 | 40.00 | K | 20.00
4x0215 | PHX/CHX Bypass defrost I-time |  | 1 | 600 | s | 60
4x0216
4x0217
4x0218
4x0219
4x0220 | Heat exchange temperature regulation P-band |  | 1.00 | 10.00 | K | 6.00
4x0221 | Heat exchange temperature regulation I-time |  | 1 | 1800 | s | 50
4x0222 | Cool exchange temperature regulation P-band |  | 1.00 | 10.00 | K | 6.00 | 1.11
4x0223 | Cool exchange temperature regulation I-time |  | 1 | 1800 | s | 50 | 1.11
4x0224
4x0225
AHU Heat/Cool
4x0226 | Re-heat P-band |  | 1.00 | 10.00 | K | 8.00
4x0227 | Re-heat I-time |  | 1 | 1800 | s | 70
4x0228 | Re-heat periodic operation of pump function |  | 0 | 1 |  | 1
4x0229 | Re-heat periodic operation of valve function |  | 0 | 1 |  | 1
4x0230 | Re-heat periodic operation interval |  | 0 | 168 | h | 24
4x0231 | Re-heat periodic operation time |  | 0 | 60 | min | 3
4x0232
4x0233
4x0234
4x0235
4x0236 | Extra regulation 1 combi coil output indication | 0=Heat, 1=Cool | 0 | 1 |  | 0 | 2.37
4x0237 | Extra regulation sequence 1 function | 0=Inactive, 1=Heat, 2=Cool, 3=Heat and Cool. | 0 | 3 |  | 0
4x0238 | Extra regulation sequence 1 output function | 0=0-10V, 1=10-0V | 0 | 1 |  | 0
4x0239 | Extra regulation sequence 1 heat max output signal | Maximum output signal setting for the extra regulation sequence. | 0.00 | 100.00 | % | 100.00
4x0240 | Extra regulation sequence 1 cool max output signal | Maximum output signal setting for the extra regulation sequence. | 0.00 | 100.00 | % | 100.00
4x0241 | Extra regulation sequence 1 heat P-band |  | 1.00 | 10.00 | K | 8
4x0242 | Extra regulation sequence 1 heat I-time |  | 1 | 1800 | s | 70
4x0243 | Extra regulation sequence 1 cool P-band |  | 1.00 | 10.00 | K | 6
4x0244 | Extra regulation sequence 1 cool I-time |  | 1 | 1800 | s | 60
4x0245 | Extra regulation 1 periodic operation of pump function |  | 0 | 1 |  | 1
4x0246 | Extra regulation 1 periodic operation of valve function |  | 0 | 1 |  | 1
4x0247 | Extra regulation 1 periodic operation interval |  | 0 | 168 | h | 24
4x0248 | Extra regulation 1 periodic operation time |  | 0 | 60 | min | 3
4x0249 | Extra regulation 1 combi coil external signal indication | 0=Heat, 1=Cool | 0 | 1 |  | 0 | 1.26
4x0250 | Extra regulation 1 combi coil external signal value | 0=Inactive, 1=Active | 0 | 1 |  | 0 | 1.26
4x0251 | Extra regulation 1 temperature protection function |  | 0 | 1 |  | 0 | 1.10
4x0252 | Extra regulation 1 temperature protection temperature |  | -50.00 | 100.00 | °C | 0.00 | 1.10
4x0253 | Extra regulation 1 temperature protection alarm delay |  | 0 | 9999 | min | 5 | 1.10
4x0254 | Season heat function | 0=Inactive, 1=Extra regulation sequence at closed input, 2=Extra regulation sequence at open input, 3=Manual mode. | 0 | 3 |  | 0
4x0255 | Season heat manual setting | 0=Re-heat, 1=Extra regulation sequence | 0 | 1 |  | 0
4x0256
4x0257
4x0258 | Cool step 1 min supply air flow limit |  | 0 | 4x0259 | l/s |  | 1.16
4x0259 | Cool step 2 min supply air flow limit |  | 4x0258 | 4x0260 | l/s |  | 1.16
4x0260 | Cool step 3 min supply air flow limit |  | 4x0259 | 3x0057 | l/s |  | 1.16
4x0261 | Cool on/off regulation function | 0=Inactive, 1=1 step, 2=2 steps, 3=3 steps. | 0 | 3 |  | 0
4x0262 | Cool SA neutral zone |  | 0.50 | 10.00 | K | 0.50
4x0263 | Cool EA neutral zone |  | 0.50 | 10.00 | K | 0.50
4x0264 | Cool outdoor temp limit 1 |  | 0.00 | 30.00 | °C | 15.00
4x0265 | Cool outdoor temp limit 2 |  | 0.00 | 30.00 | °C | 18.00
4x0266 | Cool outdoor temp limit 3 |  | 0.00 | 30.00 | °C | 20.00
4x0267 | Cool 0-10V min supply air flow limit |  | 0 | 3x0057 | l/s
4x0268 | Cool 0-10V min extract air flow limit |  | 0 | 3x0058 | l/s
4x0269 | Cool restart time | Setting of cool restart time between start-start. | 0 | 15 | min | 5
4x0270 | Cool step up delay time | Setting of on/off cooling and COOL DX time delay between steps. | 0 | 10 | min | 5
4x0271 | Cool stand still time | Setting of on/off cooling and COOL DX time delay before stop-start | 0 | 20 | min | 5
4x0272 | Cool P-band |  | 1.00 | 10.00 | K | 6
4x0273 | Cool I-time |  | 1 | 1800 | s | 60
4x0274 | Cool relay 1 periodic operation of pump function |  | 0 | 1 |  | 0
4x0275 | Cool relay 2 periodic operation of pump function |  | 0 | 1 |  | 0
4x0276 | Cool periodic operation of valve function |  | 0 | 1 |  | 0
4x0277 | Cool periodic operation interval |  | 0 | 168 | h | 24
4x0278 | Cool periodic operation time |  | 0 | 60 | min | 3
4x0279 | Cool step 1 min extract air flow limit |  | 0 | 4x0280 | l/s |  | 1.16
4x0280 | Cool step 2 min extract air flow limit |  | 4x0279 | 4x0281 | l/s |  | 1.16
4x0281 | Cool step 3 min extract air flow limit |  | 4x0280 | 3x0058 | l/s |  | 1.16
4x0282
4x0283
Summer night cool/Intermittent night heat /Morning boost
4x0284 | Summer night cool function | 0=Inactive, 1=Internal, 2=External(BMS) | 0 | 2 |  | 0 | 2.46
4x0285 | Summer night cool start time (hour) |  | 0 | 23 | h | 23
4x0286 | Summer night cool start time (minute) |  | 0 | 59 | min | 0
4x0287 | Summer night cool stop time (hour) |  | 0 | 23 | h | 23
4x0288 | Summer night cool stop time (minute) |  | 0 | 59 | min | 0
4x0289 | Summer night cool OA temp start limit |  | -5.00 | 15.00 | °C | 10.00
4x0290 | Summer night cool EA temp start limit |  | 17.00 | 27.00 | °C | 22.00
4x0291 | Summer night cool EA temp stop limit |  | 12.00 | 22.00 | °C | 16.00
4x0292 | Summer night cool SA temp set point |  | 0.00 | 20.00 | °C | 10.00
4x0293 | Summer night cool SA flow set point |  | 3x0055 | 3x0057 | l/s |  | 1.22
4x0294 | Summer night cool EA flow set point |  | 3x0056 | 3x0058 | l/s |  | 1.22
4x0295 | Summer night cool from communication | 0=Inactive, 1=Active | 0 | 1 |  | 0 | 2.46
4x0296 | Intermittent night heat function |  | 0 | 1 |  | 0
4x0297 | Intermittent night heat SA flow set point |  | 3x0055 | 3x0057 | l/s
4x0298 | Intermittent night heat SA duct pressure set point |  | 20 | 750 | Pa | 100
4x0299 | Intermittent night heat EA temp start limit |  | 5.00 | 4x0300 | °C | 16.00
4x0300 | Intermittent night heat EA temp stop limit |  | 4x0299 | 25.00 | °C | 18.00
4x0301 | Intermittent night heat SA temp set point |  | 5.00 | 50.00 | °C | 28.00
4x0302 | Intermittent night heat recirculation function |  | 0 | 1 |  | 1 | 1.12
4x0303 | Intermittent night heat EA flow set point |  | 3x0056 | 3x0058 | l/s |  | 1.12
4x0304 | Intermittent night heat EA duct pressure set point |  | 20 | 750 | Pa |  | 1.12
4x0305 | Morning boost function |  | 0 | 1 |  | 0
4x0306 | Morning boost start time (hour) |  | 0 | 23 | h | 0
4x0307 | Morning boost start time (minute) |  | 0 | 59 | min | 0
4x0308 | Morning boost air flow set point |  | 3x0055 | 3x0057 | l/s
4x0309 | Morning boost duct pressure set point |  | 20 | 750 | Pa | 100
4x0310
4x0311 | Summer night cool SA duct pressure set point |  | 20 | 750 | Pa | 100 | 1.22
4x0312 | Summer night cool EA duct pressure set point |  | 20 | 750 | Pa | 100 | 1.22
Cooling boost/heating boost
4x0313 | Cooling boost function | 0=Inactive, 1=Comfort, 2=Economy, 3=Sequence, 4=Comfort and Economy, 5=Economy and Sequence | 0 | 5 |  | 0
4x0314 | Cooling boost comfort start limit |  | 2.00 | 10.00 | K | 3.00
4x0315 | Cooling boost comfort regulation speed |  | 0.01 | 25.00 | %/s | 4.00
4x0316 | Cooling boost economy P-band |  | 1 | 10.00 | K
4x0317 | Cooling boost economy I-time |  | 1 | 1800 | s
4x0318
4x0319
4x0320 | Heating boost function |  | 0 | 1 |  | 0
4x0321 | Heating boost comfort start limit |  | 2.00 | 10.00 | K | 3.00
4x0322 | Heating boost comfort regulation speed |  | 0.01 | 25.00 | %/s | 4.00
4x0323
4x0324
Xzone function
4x0325 | Xzone heat function |  | 0 | 1 |  | 0
4x0326
4x0327 | Xzone cool function |  | 0 | 1 |  | 0
4x0328
Xzone temperature regulation
4x0329 | Xzone temperature regulation mode | 1=ERS-1, 2=ERS-2, 3=SA, 4=EA, 5=ORS, 6=ORE | 1 | 6 |  | 1
4x0330
Xzone ERS-1 reg.
4x0331 | Xzone ERS 1 step | Curve setting according to the diagram for ERS 1. | 1 | 4
4x0332 | Xzone ERS 1 diff | Supply air temp differental setting according to the diagram for ERS 1. | 1 | 7.00 | K | 2.00
4x0333 | Xzone ERS 1 breakpoint | Breakpoint temp setting according to the diagram for ERS 1. | 12.00 | 26.00 | °C | 22.00
4x0334
4x0335
Xzone ERS-2 reg.
4x0336 | Xzone ERS 2 breakpoint X1 | Breakpoint X1 setting according to the diagram for ERS 2. | 10 | 4x0337 | °C | 15.00
4x0337 | Xzone ERS 2 breakpoint X2 | Breakpoint X2 setting according to the diagram for ERS 2. | 4x0336 | 4x0338 | °C | 20.00
4x0338 | Xzone ERS 2 breakpoint X3 | Breakpoint X3 setting according to the diagram for ERS 2. | 4x0337 | 4x0339 | °C | 22.00
4x0339 | Xzone ERS 2 breakpoint X4 | Breakpoint X4 setting according to the diagram for ERS 2. | 4x0338 | 40.00 | °C | 24.00
4x0340 | Xzone ERS 2 breakpoint Y1 | Breakpoint Y1 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 20.00
4x0341 | Xzone ERS 2 breakpoint Y2 | Breakpoint Y2 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 18.00
4x0342 | Xzone ERS 2 breakpoint Y3 | Breakpoint Y3 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 14.00
4x0343 | Xzone ERS 2 breakpoint Y4 | Breakpoint Y4 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 12.00
4x0344
4x0345
Xzone SA Reg.
4x0346 | Xzone SA temperature set point | Supply air temperature setting, for supply air temp regulation mode. | 10.00 | 40.00 | °C | 21.00
4x0347
4x0348
Xzone EA Reg.
4x0349 | Xzone EA/Room temperature set point | Extract air/room temperature setting, for Extract air/room temp regulation mode. | 10.00 | 40.00 | °C | 21.00
4x0350 | Xzone SA min temp set point | Supply air min. set point during EA/room regulation mode. | 8.00 | 20.00 | °C | 16.00
4x0351 | Xzone SA max temp set point | Supply air max. set point during EA/room regulation mode. | 16.00 | 50.00 | °C | 28.00
4x0352 | Xzone EA regultaion P-band |  | 1.00 | 10.00 | K | 5.00
4x0353 | Xzone EA regultaion I-time |  | 1 | 1800 | s | 180
Xzone ORS Reg.
4x0354 | Xzone ORS breakpoint X1 | Breakpoint X1 setting according to the diagram for ORS. | -5.00 | 4x0355 | °C | -20.00
4x0355 | Xzone ORS breakpoint X2 | Breakpoint X2 setting according to the diagram for ORS. | 4x354 | 4x0356 | °C | -10.00
4x0356 | Xzone ORS breakpoint X3 | Breakpoint X3 setting according to the diagram for ORS. | 4x355 | 4x0357 | °C | 10.00
4x0357 | Xzone ORS breakpoint X4 | Breakpoint X4 setting according to the diagram for ORS. | 4x356 | 50.00 | °C | 20.00
4x0358 | Xzone ORS breakpoint Y1 | Breakpoint Y1 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
4x0359 | Xzone ORS breakpoint Y2 | Breakpoint Y2 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
4x0360 | Xzone ORS breakpoint Y3 | Breakpoint Y3 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
4x0361 | Xzone ORS breakpoint Y4 | Breakpoint Y4 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
4x0362
4x0363
Xzone ORE Reg.
4x0364 | Xzone ORE breakpoint X1 | Breakpoint X1 setting according to the diagram for ORE. | -5.00 | 4x0365 | °C | -20.00
4x0365 | Xzone ORE breakpoint X2 | Breakpoint X2 setting according to the diagram for ORE. | 4x364 | 4x0366 | °C | -10.00
4x0366 | Xzone ORE breakpoint X3 | Breakpoint X3 setting according to the diagram for ORE. | 4x365 | 4x0367 | °C | 10.00
4x0367 | Xzone ORE breakpoint X4 | Breakpoint X4 setting according to the diagram for ORE. | 4x366 | 50.00 | °C | 20.00
4x0368 | Xzone ORE breakpoint Y1 | Breakpoint Y1 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
4x0369 | Xzone ORE breakpoint Y2 | Breakpoint Y2 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
4x0370 | Xzone ORE breakpoint Y3 | Breakpoint Y3 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
4x0371 | Xzone ORE breakpoint Y4 |  | 10.00 | 40.00 | °C | 21.50
4x0372
4x0373
Xzone external sensors
4x0374 | Xzone external room sensor 1 function |  | 0 | 1 |  | 0
4x0375 | Xzone external room sensor 2 function |  | 0 | 1 |  | 0
4x0376 | Xzone external room sensor 3 function |  | 0 | 1 |  | 0
4x0377 | Xzone external room sensor 4 function |  | 0 | 1 |  | 0
4x0378 | Xzone external room sensors measurement function | 0=Average, 1=Min, 2=Max | 0 | 2 |  | 0
4x0379 | Xzone external room temp from BMS function |  | 0 | 1 |  | 0
4x0380 | Xzone external room temp from BMS |  | -55.00 | 125.00 | °C | 0.00
4x0381 | Xzone external room temp from BMS alarm time |  | 0 | 9999 | min | 5
4x0382
4x0383
Xzone Heat/Cool
4x0384 | Xzone reheat P-band |  | 1.00 | 10.00 | K | 8.00
4x0385 | Xzone reheat I-time |  | 1 | 1800 | s | 70
4x0386 | Xzone reheat periodic operation of pump function |  | 0 | 1 |  | 1
4x0387 | Xzone reheat periodic operation of valve function |  | 0 | 1 |  | 1
4x0388 | Xzone reheat periodic operation interval |  | 0 | 168 | h | 24
4x0389 | Xzone reheat periodic operation time |  | 0 | 60 | min | 3
4x0390 | Xzone combi coil module A external signal indication | 0=Heat, 1=Cool | 0 | 1 |  | 0 | 2.43
4x0391 | Xzone combi coil module A output indication | 0=Heat, 1=Cool | 0 | 1 |  | 0 | 2.43
4x0392 | Xzone combi coil module A external signal value | 0=Inactive, 1=Active | 0 | 1 |  | 0 | 2.43
4x0393
4x0394
4x0395 | Xzone Cool on/off regulation function | 0=Inactive, 1=1 step, 2=2 steps, 3=3 steps. | 0 | 3 |  | 0
4x0396 | Xzone Cool SA neutral zone |  | 0.50 | 10.00 | K | 0.50
4x0397 | Xzone Cool EA neutral zone |  | 0.50 | 10.00 | K | 0.50
4x0398 | Xzone Cool P-band |  | 1.00 | 10.00 | K | 6.00
4x0399 | Xzone Cool I-time |  | 1 | 1800 | s | 60
4x0400 | Xzone Cool relay 1 periodic operation of pump function |  | 0 | 1 |  | 0
4x0401 | Xzone Cool relay 2 periodic operation of pump function |  | 0 | 1 |  | 0
4x0402 | Xzone Cool periodic operation of valve function |  | 0 | 1 |  | 0
4x0403 | Xzone Cool periodic operation interval |  | 0 | 168 | h | 24
4x0404 | Xzone Cool periodic operation time |  | 0 | 60 | min | 3
4x0405 | Xzone combi coil module B external signal indication | 0=Heat, 1=Cool | 0 | 1 |  | 0 | 2.43
4x0406 | Xzone combi coil module B output indication | 0=Heat, 1=Cool | 0 | 1 |  | 0 | 2.43
4x0407 | Xzone combi coil module B external signal value | 0=Inactive, 1=Active | 0 | 1 |  | 0 | 2.43
4x0408
4x0409
Pre-heat
4x0410 | Pre-heat function |  | 0 | 1 |  | 0
4x0411 | Pre-heat temperature set point |  | -40.00 | 40.00 | °C | 5.00
4x0412 | Pre-heat P-band |  | 1.00 | 10.00 | K | 8.00
4x0413 | Pre-heat I-time |  | 1 | 1800 | s | 70
4x0414 | Pre-heat periodic operation of pump function |  | 0 | 1 |  | 1
4x0415 | Pre-heat periodic operation of valve function |  | 0 | 1 |  | 1
4x0416 | Pre-heat periodic operation interval
4x0417 | Pre-heat periodic operation time
4x0418
4x0419
4x0420
4x0421
4x0422
ReCO2
4x0423 | ReCO2-CO2 function | 0=Inactive, 1=CO2, 2=CO2 and air flow boost | 0 | 2 |  | 0
4x0424 | ReCO2 temperature regulation sequence function | 0=Inactive, 1=Heat, 2=Cool, 3=Heat and Cool. | 0 | 3 |  | 0
4x0425 | ReCO2 Calibration |  | 0 | 1 |  | 0
4x0426 | ReCO2-CO2 set point |  | 0.00 | 100.00 | % | 50.00
4x0427 | ReCO2 min. outdoor air |  | 0 | 3x0057 | l/s
4x0428 | ReCO2 min. exhaust air |  | 0 | 3x0058 | l/s
4x0429 | ReCO2-CO2 P-band |  | 1.00 | 100.00 | % | 50.00
4x0430 | ReCO2-CO2 I-time |  | 1 | 1800 | s | 60
4x0431 | ReCO2-CO2 air flow boost reg. P-band |  | 10.00 | 100.00 | % | 50.00
4x0432 | ReCO2-CO2 air flow boost reg. I-time |  | 1 | 1800 | s | 60
4x0433 | ReCO2 heat P-band |  | 1.00 | 10.00 | K | 7.00
4x0434 | ReCO2 heat I-time |  | 1 | 1800 | s | 70
4x0435 | ReCO2 cool P-band |  | 1.00 | 10.00 | K | 6.00
4x0436 | ReCO2 cool I-time |  | 1 | 1800 | s | 60
4x0437 | ReCO2-CO2 ppm set point |  | 0 | 10000 | ppm | 1000 | 1.28
4x0438 | ReCO2-CO2 ppm P-band |  | 100 | 10000 | ppm | 600 | 1.28
4x0439 | ReCO2-VOC ppm set point |  | 0 | 10000 | ppm | 1500 | 1.28
4x0440 | ReCO2-VOC ppm P-band |  | 100 | 10000 | ppm | 1000 | 1.28
Humidity/VOC
4x0441 | Humidifying function | 0=Inactive, 1=on/off, 2=0-10V | 0 | 2 |  | 0
4x0442 | Humidifying sensor | 0=SA, 1=EA | 0 | 1 |  | 0
4x0443 | Humidifying on/off start level |  | 10.00 | 4x0444 | %RH | 40.00
4x0444 | Humidifying on/off stop level |  | 4x0443 | 95.00 | %RH | 45.00
4x0445
4x0446
4x0447
4x0448 | Humidifying 0-10V set point |  | 10.00 | 95.00 | %RH | 30.00
4x0449 | Humidifying 0-10V SA max set point |  | 10.00 | 95.00 | %RH | 80.00
4x0450 | Humidifying 0-10V SA P-band |  | 1.00 | 200.00 | %RH | 60.00
4x0451 | Humidifying 0-10V SA I-time |  | 1 | 1800 | s | 30
4x0452 | Humidifying 0-10V EA P-band |  | 1.00 | 200.00 | %RH | 60.00
4x0453 | Humidifying 0-10V EA I-time |  | 1 | 1800 | s | 180
4x0454
4x0455
4x0456
4x0457 | Dehumidifying function | 0=Inactive, 1=SA, 2=EA, 3=Room(2.42) | 0 | 3 |  | 1 | 1.12
4x0458 | Dehumidifying SA set point |  | 10.00 | 90.00 | %RH | 50.00
4x0459 | Heat exchange active in dehumidifying sequence |  | 0 | 1 |  | 0
4x0460 | Dehumidifying EA set point |  | 10.00 | 90.00 | %RH | 50.00 | 1.18
4x0461
4x0462
4x0463
4x0464
4x0465 | VOC sensor function | 0=Inactive, 1=Monitoring only, 2=Monitoring and regulation | 0 | 2 |  | 0 | 1.17
4x0466
4x0467
4x0468
COOL DX
4x0469 | COOL DX Function | 0=Inactive, 1=Economy, 2=Comfort, 3=Top | 0 | 3 |  | 0
4x0470 | COOL DX Low pressure stop limit |  | 1.00 | 10.00 | Bar | 3.00
4x0471 | COOL DX High pressure stop limit |  | 25.00 | 40.00 | Bar | 39.00
4x0472 | COOL DX Restart time | Time setting between start - start | 5 | 15 | min | 5
Exhaust heat
4x0473 | Constant exhaust air temperature function | 0=Inactive, 1=Active | 0 | 1 |  | 0 | 2.43
4x0474 | Exhaust heat temperature set point | Exhaust heat temperature set point | -40.00 | 40.00 | °C | 5.00 | 2.43
4x0475 | Exhaust heat P-band | Exhaust heat P-band | 1.00 | 10.00 | K | 8.00 | 2.43
4x0476 | Exhaust heat I-time | Exhaust heat I-time | 1 | 1800 | s | 70 | 2.43
4x0477 | Exhaust heat periodic operation of pump function | Exhaust heat periodic operation of pump function | 0 | 1 |  | 1 | 2.43
4x0478 | Exhaust heat periodic operation of valve function | Exhaust heat periodic operation of valve function | 0 | 1 |  | 1 | 2.43
4x0479 | Exhaust heat periodic operation interval | Exhaust heat periodic operation interval | 0 | 168 | h | 24 | 2.43
4x0480 | Exhaust heat periodic operation time | Exhaust heat periodic operation time | 0 | 60 | min | 3 | 2.43
SMART Link
4x0481 | SMART Link Function | 0=Inactive, 1=Water based heat pump, 2=Water based chiller, 3=Water based reversible, 4=DX based heat pump, 5=DX based chiller, 6=DX based reversible, | 0 | 6 |  | 0
4x0482 | SMART Link WB Heat temperature set point |  | 3x0299 | 3x0300 | °C | 40.0
4x0483 | SMART Link WB Heat temperature heat zone |  | 1.0 | 10.0 | K | 3.0
4x0484 | SMART Link WB Cool temperature set point |  | 3x0301 | 3x0302 | °C | 12.0
4x0485 | SMART Link WB Cool temperature heat zone |  | 1.0 | 10.0 | K | 2.0
4x0486
4x0487
4x0488
4x0489 | SMART Link WB Cooling Optimize function |  | 0 | 1 |  | 0 | 1.26
4x0490 | SMART Link WB Heating Optimize function |  | 0 | 1 |  | 0
4x0491 | SMART Link WB Optimize valve upper limit |  | 5.0 | 90.0 | % | 80.0
4x0492 | SMART Link WB Optimize valve lower limit |  | 70.0 | 100.0 | % | 100.0
4x0493 | SMART Link WB Optimize time delay |  | 30 | 32000 | s | 60
4x0494 | SMART Link WB Optimize heat regulation speed |  | 0.001 | 1.000 | K/s | 0.005
4x0495 | SMART Link WB Optimize cool regulation speed |  | 0.001 | 1.000 | K/s | 0.010
4x0496
4x0497
4x0498
4x0499
4x0500
4x0501
4x0502
4x0503
4x0504 | AQUA Link Function |  | 0 | 1
4x0505 | AQUA Link Pump alarm function | 0=Inactive, 1=alarm at closed contact, 2=Alarm at open contact, 3=Alarm when in -and output are unequal (contactor function). | 0 | 3
4x0506
4x0507
4x0508
4x0509
4x0510 | SMART Link DX Amount of units |  | 0 | 4 |  | 1
4x0511
4x0512
4x0513
4x0514
4x0515 | SMART Link DX Time delay before defrost |  | 30 | 900 | s | 90
4x0516
4x0517
4x0518
4x0519 | SMART Link OA temp limit |  | -50.00 | 50.00 | °C | -30.00 | 1.12
4x0520
AYC
4x0521 | AYC Function | 0=Inactive, 1=Chilled water, 2=Heated water, 3=Chilled and heated water | 0 | 3 |  | 0
4x0522
4x0523
4x0524 | AYC Heated water temp set point |  | 10.00 | 80.00 | °C | 30.00
4x0525
4x0526 | AYC Heated water OA temp for start of pump |  | -40.00 | 40.00 |  | 15.00
4x0527 | AYC Heated water OA temp for stop of pump |  | -40.00 | 40.00 |  | 18.00
4x0528 | AYC Heated water alarm function for pump | 0=Inactive, 1= Alarm at open contact, 2=Alarm at closed contact, 3=Contactor | 0 | 3 |  | 0 | 1.10
4x0529
4x0530 | AYC Heated water periodic operation of pump |  | 0 | 1 |  | 1
4x0531 | AYC Heated water periodic operation of valve |  |  | 1 |  | 0
4x0532 | AYC Heated water periodic operation interval |  | 0 | 168 | h | 24
4x0533 | AYC Heated water periodic operation time |  | 0 | 60 | min | 3
4x0534
4x0535
4x0536 | AYC Heated water OA temp compensation |  | 0 | 1 |  | 0
4x0537 | AYC Heated water OA temp compensation X1 |  | -40.00 | 4x0538 | °C | -20.00
4x0538 | AYC Heated water OA temp compensation X2 |  | 4x0537 | 4x0539 | °C | 0.00
4x0539 | AYC Heated water OA temp compensation X3 |  | 4x0538 | 4x0540 | °C | 5.00
4x0540 | AYC Heated water OA temp compensation X4 |  | 4x0539 | 40.00 | °C | 15.00
4x0541 | AYC Heated water OA temp compensation Y1 |  | -40.00 | 40.00 | °C | 40.00
4x0542 | AYC Heated water OA temp compensation Y2 |  | -40.00 | 40.00 | °C | 30.00
4x0543 | AYC Heated water OA temp compensation Y3 |  | -40.00 | 40.00 | °C | 20.00
4x0544 | AYC Heated water OA temp compensation Y4 |  | -40.00 | 40.00 | °C | 15.00
4x0545
4x0546
4x0547 | AYC Heated water room temp compensation function |  | 0 | 1 |  | 0
4x0548 | AYC Heated water room temp compensation at night | 0=Enabled during night, 1=Disabled during night | 0 | 1 |  | 0
4x0549 | AYC Heated water room temp compensation temperature |  | 0.00 | 40.00 | °C | 21.00
4x0550 | AYC Heated water room temp compensation P-band |  | 1.00 | 10.00 | K | 5.00
4x0551
4x0552
4x0553 | AYC Heated water night temp compensation function |  | 0 | 1 |  | 0
4x0554 | AYC Heated water night temp compensation temp |  | -10.00 | 10.00 | K | -2.00
4x0555 | AYC Heated water night temp compensation time 1 (days) | 0=Inactive, 1=Monday, 2=Tuesday, 3=Wednesday, 4=Thursday, 5=Friday, 6=Saturday, 7=Sunday, 8=Monday to Friday, 9= Monday to Sunday, 10=Saturday to Sunday. | 0 | 10 |  | 0
4x0556 | AYC Heated water night temp compensation start time 1 (hour) |  | 0 | 23 | h | 0
4x0557 | AYC Heated water night temp compensation start time 1 (minutes) |  | 0 | 59 | min | 0
4x0558 | AYC Heated water night temp compensation stop time 1 (hour) |  | 0 | 23 | h | 0
4x0559 | AYC Heated water night temp compensation stop time 1 (minutes) |  | 0 | 59 | min | 0
4x0560
4x0561
4x0562 | AYC Heated water night temp compensation time 2 (days) | 0=Inactive, 1=Monday, 2=Tuesday, 3=Wednesday, 4=Thursday, 5=Friday, 6=Saturday, 7=Sunday, 8=Monday to Friday, 9= Monday to Sunday, 10=Saturday to Sunday. | 0 | 10 |  | 0
4x0563 | AYC Heated water night temp compensation start time 2 (hour) |  | 0 | 23 | h | 0
4x0564 | AYC Heated water night temp compensation start time 2 (minutes) |  | 0 | 59 | min | 0
4x0565 | AYC Heated water night temp compensation stop time 2 (hour) |  | 0 | 23 | h | 0
4x0566 | AYC Heated water night temp compensation stop time 2 (minutes) |  | 0 | 59 | min | 0
4x0567
4x0568
4x0569 | AYC Heated water P-band |  | 1.00 | 40..00 | K | 15.00
4x0570 | AYC Heated water I-time |  | 1 | 600 | s | 60
4x0571
4x0572 | AYC Chilled water temp set point |  | 10.00 | 80.00 | °C | 30.00
4x0573
4x0574
4x0575 | AYC Chilled water OA temp for start of pump |  | -40.00 | 40.00 |  | 15.00
4x0576 | AYC Chilled water OA temp for stop of pump |  | -40.00 | 40.00 |  | 18.00
4x0577 | AYC Chilled water alarm function for pump | 0=Inactive, 1= Alarm at open contact, 2=Alarm at closed contact, 3=Contactor | 0 | 3 |  | 0 | 1.10
4x0578
4x0579 | AYC Chilled water periodic operation of pump |  | 0 | 1 |  | 1
4x0580 | AYC Chilled water periodic operation of valve |  |  | 1 |  | 0
4x0581 | AYC Chilled water periodic operation interval |  | 0 | 168 | h | 24
4x0582 | AYC Chilled water periodic operation time |  | 0 | 60 | min | 3
4x0583
4x0584
4x0585 | AYC Chilled water OA temp compensation |  | 0 | 1 |  | 0
4x0586 | AYC Chilled water OA temp compensation X1 |  | -40.00 | 4x0587 | °C | -20.00
4x0587 | AYC Chilled water OA temp compensation X2 |  | 4x0586 | 4x0588 | °C | 0.00
4x0588 | AYC Chilled water OA temp compensation X3 |  | 4x0587 | 4x0589 | °C | 5.00
4x0589 | AYC Chilled water OA temp compensation X4 |  | 4x0588 | 40.00 | °C | 15.00
4x0590 | AYC Chilled water OA temp compensation Y1 |  | -40.00 | 40.00 | °C | 40.00
4x0591 | AYC Chilled water OA temp compensation Y2 |  | -40.00 | 40.00 | °C | 30.00
4x0592 | AYC Chilled water OA temp compensation Y3 |  | -40.00 | 40.00 | °C | 20.00
4x0593 | AYC Chilled water OA temp compensation Y4 |  | -40.00 | 40.00 | °C | 15.00
4x0594
4x0595
4x0596 | AYC Chilled water room temp compensation function |  | 0 | 1 |  | 0
4x0597 | AYC Chilled water room temp compensation at night | 0=Enabled during night, 1=Disabled during night | 0 | 1 |  | 0
4x0598 | AYC Chilledwater room temp compensation temperature |  | 0.00 | 40.00 | °C | 21.00
4x0599 | AYC Chilled water room temp compensation P-band |  | 1.00 | 10.00 | K | 5.00
4x0600
4x0601
4x0602 | AYC Chilled water night temp compensation function |  | 0 | 1 |  | 0
4x0603 | AYC Chilled water night temp compensation temp |  | -10.00 | 10.00 | K | -2.00
4x0604 | AYC Chilled water night temp compensation time 1 (days) | 0=Inactive, 1=Monday, 2=Tuesday, 3=Wednesday, 4=Thursday, 5=Friday, 6=Saturday, 7=Sunday, 8=Monday to Friday, 9= Monday to Sunday, 10=Saturday to Sunday. | 0 | 10 |  | 0
4x0605 | AYC Chilled water night temp compensation start time 1 (hour) |  | 0 | 23 | h | 0
4x0606 | AYC Chilled water night temp compensation start time 1 (minutes) |  | 0 | 59 | min | 0
4x0607 | AYC Chilled water night temp compensation stop time 1 (hour) |  | 0 | 23 | h | 0
4x0608 | AYC Chilled water night temp compensation stop time 1 (minutes) |  | 0 | 59 | min | 0
4x0609
4x0610
4x0611 | AYC Chilled water night temp compensation time 2 (days) | 0=Inactive, 1=Monday, 2=Tuesday, 3=Wednesday, 4=Thursday, 5=Friday, 6=Saturday, 7=Sunday, 8=Monday to Friday, 9= Monday to Sunday, 10=Saturday to Sunday. | 0 | 10 |  | 0
4x0612 | AYC Chilled water night temp compensation start time 2 (hour) |  | 0 | 23 | h | 0
4x0613 | AYC Chilled water night temp compensation start time 2 (minutes) |  | 0 | 59 | min | 0
4x0614 | AYC Chilledwater night temp compensation stop time 2 (hour) |  | 0 | 23 | h | 0
4x0615 | AYC Chilled water night temp compensation stop time 2 (minutes) |  | 0 | 59 | min | 0
4x0616
4x0617
4x0618 | AYC Chilled water dew point compensation air flow boost |  | 0 | 1 |  | 0
4x0619 | AYC Chilled water dew point compensation neutral zone |  | 0 | 5.00 | K | 2.00
4x0620 | AYC Chilled water dew point compensation regulation speed | Percent air flow boost of each increased chilled water set point. | 0 | 30.00 | %/K | 10.00
4x0621
4x0622
4x0623 | AYC Chilled water P-band |  | 1.00 | 40..00 | K | 15.00
4x0624 | AYC Chilled water I-time |  | 1 | 600 | s | 60
4x0625
4x0626
4x0627
4x0628
4x0629
4x0630
4x0631
4x0632
4x0633
4x0634
4x0635
4x0636
Optimize
4x0637 | Optimize function |  | 0 | 1 |  | 0
4x0638 | Optimize SA pressure set point |  | 20.0 | 750.0 | Pa | 0
4x0639 | Optimize EA pressure set point |  | 20.0 | 750.0 | Pa | 0
4x0640
4x0641
4x0642
4x0643
4x0644
4x0645
4x0646
4x0647
4x0648
4x0649
4x0650
4x0651
4x0652
4x0653
4x0654
MIRU Control
4x0655
4x0656
4x0657
4x0658
4x0659
4x0660 | MIRU Control 1 function | 0=Inactive, 1=Parallel start, 2=Parallell low / high speed , 3=Parallel start and Low / high speed | 0 | 3 |  | 0
4x0661 | MIRU Control 2 function | 0=Inactive, 1=Parallel start, 2=Parallell low / high speed , 3=Parallel start and Low / high speed | 0 | 3 |  | 0
4x0662 | MIRU Control 3 function | 0=Inactive, 1=Parallel start, 2=Parallell low / high speed , 3=Parallel start and Low / high speed | 0 | 3 |  | 0
4x0663 | MIRU Control 4 function | 0=Inactive, 1=Parallel start, 2=Parallell low / high speed , 3=Parallel start and Low / high speed | 0 | 3 |  | 0
4x0664 | MIRU Control 5 function | 0=Inactive, 1=Parallel start, 2=Parallell low / high speed , 3=Parallel start and Low / high speed | 0 | 3 |  | 0
4x0665 | MIRU Control 6 function | 0=Inactive, 1=Parallel start, 2=Parallell low / high speed , 3=Parallel start and Low / high speed | 0 | 3 |  | 0
4x0666 | MIRU Control 7 function | 0=Inactive, 1=Parallel start, 2=Parallell low / high speed , 3=Parallel start and Low / high speed | 0 | 3 |  | 0
4x0667 | MIRU Control 8 function | 0=Inactive, 1=Parallel start, 2=Parallell low / high speed , 3=Parallel start and Low / high speed | 0 | 3 |  | 0
4x0668 | MIRU Control 9 function | 0=Inactive, 1=Parallel start, 2=Parallell low / high speed , 3=Parallel start and Low / high speed | 0 | 3 |  | 0
4x0669 | MIRU Control 10 function | 0=Inactive, 1=Parallel start, 2=Parallell low / high speed , 3=Parallel start and Low / high speed | 0 | 3 |  | 0
4x0670
4x0671 | MIRU Control 1 balanced air flow function | 0=Inactive, 1=SA, 2=EA. | 0 | 2 |  | 0
4x0672 | MIRU Control 1 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
4x0673 | MIRU Control 1 High speed duct pressure set point |  | 0 | 750 | Pa | 200
4x0674 | MIRU Control 1 Low speed air flow set point |  | 3x0400 | 3x0401 | l/s
4x0675 | MIRU Control 1 High speed air flow set point |  | 3x0400 | 3x0401 | l/s
4x0676 | MIRU Control 1 offset factor for slave controlled air flow | Offset factor | 2.00 | 20.00 | % | 10.00 | 2.42
4x0677 | MIRU Control 1 fixed flow offset for slave controlled SA flow |  | 0 | 3x0401 | l/s |  | 2.42
4x0678
4x0679 | MIRU Control 2 balanced air flow function | 0=Inactive, 1=SA, 2=EA. | 0 | 2 |  | 0
4x0680 | MIRU Control 2 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
4x0681 | MIRU Control 2 High speed duct pressure set point |  | 0 | 750 | Pa | 200
4x0682 | MIRU Control 2 Low speed air flow set point |  | 3x0417 | 3x0418 | l/s
4x0683 | MIRU Control 2 High speed air flow set point |  | 3x0417 | 3x0418 | l/s
4x0684 | MIRU Control 2 offset factor for slave controlled air flow | Offset factor | 2.00 | 20.00 | % | 10.00 | 2.42
4x0685 | MIRU Control 2 fixed flow offset for slave controlled SA flow |  | 0 | 3x0418 | l/s |  | 2.42
4x0686
4x0687 | MIRU Control 3 balanced air flow function | 0=Inactive, 1=SA, 2=EA. | 0 | 2 |  | 0
4x0688 | MIRU Control 3 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
4x0689 | MIRU Control 3 High speed duct pressure set point |  | 0 | 750 | Pa | 200
4x0690 | MIRU Control 3 Low speed air flow set point |  | 3x0434 | 3x0435 | l/s
4x0691 | MIRU Control 3 High speed air flow set point |  | 3x0434 | 3x0435 | l/s
4x0692 | MIRU Control 3 offset factor for slave controlled air flow | Offset factor | 2.00 | 20.00 | % | 10.00 | 2.42
4x0693 | MIRU Control 3 fixed flow offset for slave controlled SA flow |  | 0 | 3x0435 | l/s |  | 2.42
4x0694
4x0695 | MIRU Control 4 balanced air flow function | 0=Inactive, 1=SA, 2=EA. | 0 | 2 |  | 0
4x0696 | MIRU Control 4 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
4x0697 | MIRU Control 4 High speed duct pressure set point |  | 0 | 750 | Pa | 200
4x0698 | MIRU Control 4 Low speed air flow set point |  | 3x0451 | 3x0452 | l/s
4x0699 | MIRU Control 4 High speed air flow set point |  | 3x0451 | 3x0452 | l/s
4x0700
4x0701
4x0702
4x0703 | MIRU Control 5 balanced air flow function | 0=Inactive, 1=SA, 2=EA. | 0 | 2 |  | 0
4x0704 | MIRU Control 5 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
4x0705 | MIRU Control 5 High speed duct pressure set point |  | 0 | 750 | Pa | 200
4x0706 | MIRU Control 5 Low speed air flow set point |  | 3x0468 | 3x0469 | l/s
4x0707 | MIRU Control 5 High speed air flow set point |  | 3x0468 | 3x0469 | l/s
4x0708
4x0709
4x0710
4x0711 | MIRU Control 6 balanced air flow function | 0=Inactive, 1=SA, 2=EA. | 0 | 2 |  | 0
4x0712 | MIRU Control 6 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
4x0713 | MIRU Control 6 High speed duct pressure set point |  | 0 | 750 | Pa | 200
4x0714 | MIRU Control 6 Low speed air flow set point |  | 3x0485 | 3x0486 | l/s
4x0715 | MIRU Control 6 High speed air flow set point |  | 3x0485 | 3x0486 | l/s
4x0716
4x0717
4x0718
4x0719 | MIRU Control 7 balanced air flow function | 0=Inactive, 1=SA, 2=EA. | 0 | 2 |  | 0
4x0720 | MIRU Control 7 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
4x0721 | MIRU Control 7 High speed duct pressure set point |  | 0 | 750 | Pa | 200
4x0722 | MIRU Control 7 Low speed air flow set point |  | 3x0502 | 3x0503 | l/s
4x0723 | MIRU Control 7 High speed air flow set point |  | 3x0502 | 3x0503 | l/s
4x0724
4x0725
4x0726
4x0727 | MIRU Control 8 balanced air flow function | 0=Inactive, 1=SA, 2=EA. | 0 | 2 |  | 0
4x0728 | MIRU Control 8 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
4x0729 | MIRU Control 8 High speed duct pressure set point |  | 0 | 750 | Pa | 200
4x0730 | MIRU Control 8 Low speed air flow set point |  | 3x0519 | 3x0520 | l/s
4x0731 | MIRU Control 8 High speed air flow set point |  | 3x0519 | 3x0520 | l/s
4x0732
4x0733
4x0734
4x0735 | MIRU Control 9 balanced air flow function | 0=Inactive, 1=SA, 2=EA. | 0 | 2 |  | 0
4x0736 | MIRU Control 9 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
4x0737 | MIRU Control 9 High speed duct pressure set point |  | 0 | 750 | Pa | 200
4x0738 | MIRU Control 9 Low speed air flow set point |  | 3x0536 | 3x0537 | l/s
4x0739 | MIRU Control 9 High speed air flow set point |  | 3x0536 | 3x0537 | l/s
4x0740
4x0741
4x0742
4x0743 | MIRU Control 10 balanced air flow function | 0=Inactive, 1=SA, 2=EA. | 0 | 2 |  | 0
4x0744 | MIRU Control 10 Low speed duct pressure set point |  | 0 | 750 | Pa | 100
4x0745 | MIRU Control 10 High speed duct pressure set point |  | 0 | 750 | Pa | 200
4x0746 | MIRU Control 10 Low speed air flow set point |  | 3x0553 | 3x0554 | l/s
4x0747 | MIRU Control 10 High speed air flow set point |  | 3x0553 | 3x0554 | l/s
4x0748
4x0749
4x0750
4x0751
Efficiency measurement
4x0752 | Delta temperature alarm limit |  | 3.00 | 20.00 | K | 6.00 | 1.23
4x0753 | Efficiency alarm limit |  | 10.00 | 70.00 | % | 50.00 | 1.23
Neutral zone
4x0754 | Extra regulation sequence 1 heat neutral zone |  | 0 | 10.00 | K | 0 | 1.32
4x0755 | Extra regulation sequence 2 heat neutral zone |  | 0 | 10.00 | K | 0 | 1.32
4x0756 | ReCO2 heat neutral zone |  | 0 | 10.00 | K | 0 | 1.32
4x0757 | H/C heat neutral zone |  | 0 | 10.00 | K | 0 | 1.32
4x0758 | Re-heat neutral zone |  | 0 | 10.00 | K | 0 | 1.32
4x0759 | Extra regulation sequence 1 cool neutral zone |  | 0 | 10.00 | K | 0 | 1.32
4x0760 | Extra regulation sequence 2 cool neutral zone |  | 0 | 10.00 | K | 0 | 1.32
4x0761 | ReCO2 cool neutral zone |  | 0 | 10.00 | K | 0 | 1.32
4x0762 | H/C cool neutral zone |  | 0 | 10.00 | K | 0 | 1.32
4x0763 | Cool neutral zone |  | 0 | 10.00 | K | 0 | 1.32
4x0764 | Cooling boost neutral zone |  | 0 | 10.00 | K | 0 | 1.32
4x0765 | Heat neutral zone function | 0=Set point, 1=Start limit. | 0 | 1 |  | 0 | 1.32
4x0766 | Cool neutral zone function | 0=Set point, 1=Start limit. | 0 | 1 |  | 0 | 1.32
4x0767
4x0768
4x0769
4x0770
4x0771
4x0772
4x0773
4x0774
Night temp compensation
4x0775 | Night temp compensation function |  | 0 | 1 |  | 0 | 1.31
4x0776 | Night temp compensation temp |  | -10.00 | 0 | K | -2.00 | 1.31
4x0777 | Night temp compensation time 1 (days) | 0=Inactive, 1=Monday, 2=Tuesday, 3=Wednesday, 4=Thursday, 5=Friday, 6=Saturday, 7=Sunday, 8=Monday to Friday, 9= Monday to Sunday, 10=Saturday to Sunday. | 0 | 10 |  | 0 | 1.31
4x0778 | Night temp compensation start time 1 (hour) |  | 0 | 23 | h | 0 | 1.31
4x0779 | Night temp compensation start time 1 (minute) |  | 0 | 59 | min | 0 | 1.31
4x0780 | Night temp compensation stop time 1 (hour) |  | 0 | 23 | h | 0 | 1.31
4x0781 | Night temp compensation stop time 1 (minute) |  | 0 | 59 | min | 0 | 1.31
4x0782 | Night temp compensation time 2 (days) | 0=Inactive, 1=Monday, 2=Tuesday, 3=Wednesday, 4=Thursday, 5=Friday, 6=Saturday, 7=Sunday, 8=Monday to Friday, 9= Monday to Sunday, 10=Saturday to Sunday. | 0 | 10 |  | 0 | 1.31
4x0783 | Night temp compensation start time 2 (hour) |  | 0 | 23 | h | 0 | 1.31
4x0784 | Night temp compensation start time 2 (minute) |  | 0 | 59 | min | 0 | 1.31
4x0785 | Night temp compensation stop time 2 (hour) |  | 0 | 23 | h | 0 | 1.31
4x0786 | Night temp compensation stop time 2 (minute) |  | 0 | 59 | min | 0 | 1.31
4x0787
4x0788
4x0789
4x0790
4x0791
4x0792
Operation level settings
4x0793 | Communication operation level | 0=auto, 1=total stop, 2=low speed, 3=high speed, 4=normal stop, 5=extended normal stop. | 0 | 5 |  | 0
4x0794
4x0795
4x0796
4x0797
4x0798
4x0799
BMS I/O-modules
4x0800 | External operation I/O-module A, analogue output |  | 0.00 | 100.00 | % | 0.00 | 1.20
4x0801 | External operation I/O-module B, analogue output |  | 0.00 | 100.00 | % | 0.00 | 1.20
4x0802 | External operation I/O-module C, analogue output |  | 0.00 | 100.00 | % | 0.00 | 1.20
4x0803
4x0804
4x0805
4x0806
4x0807
4x0808
4x0809
4x0810
4x0811
4x0812
4x0813
4x0814
4x0815
Reserved
4x0816 | Extra regulation sequence 2 function | 0=Inactive, 1=Heat, 2=Cool, 3=Heat and Cool. | 0 | 3 |  | 0 | 1.13
4x0817 | Extra regulation sequence 2 output function | 0=0-10V, 1=10-0V | 0 | 1 |  | 0 | 1.13
4x0818 | Extra regulation sequence 2 heat max output signal | Maximum output signal setting for the extra regulation sequence. | 0.00 | 100.00 | % | 100.00 | 1.13
4x0819 | Extra regulation sequence 2 cool max output signal | Maximum output signal setting for the extra regulation sequence. | 0.00 | 100.00 | % | 100.00 | 1.13
4x0820 | Extra regulation sequence 2 heat P-band |  | 1.00 | 10.00 | K | 8 | 1.13
4x0821 | Extra regulation sequence 2 heat I-time |  | 1 | 1800 | s | 70 | 1.13
4x0822 | Extra regulation sequence 2 cool P-band |  | 1.00 | 10.00 | K | 6 | 1.13
4x0823 | Extra regulation sequence 2 cool I-time |  | 1 | 1800 | s | 60 | 1.13
4x0824 | Extra regulation 2 periodic operation of pump function |  | 0 | 1 |  | 1 | 1.13
4x0825 | Extra regulation 2 periodic operation of valve function |  | 0 | 1 |  | 1 | 1.13
4x0826 | Extra regulation 2 periodic operation interval |  | 0 | 168 | h | 24 | 1.13
4x0827 | Extra regulation 2 periodic operation time |  | 0 | 60 | min | 3 | 1.13
4x0828 | Extra regulation 2 combi coil external signal indication | 0=Heat, 1=Cool | 0 | 1 |  | 0 | 1.26
4x0829 | Extra regulation 2 combi coil external signal value | 0=Inactive, 1=Active | 0 | 1 |  | 0 | 1.26
4x0830 | Seasonal controlled supply air |  | 0.00 | 40.00 | C | 21.00 | 1.28
4x0831 | Seasonal controlled extract air/room temp |  | 0.00 | 40.00 | C | 21.00 | 1.28
4x0832 | Seasonal controlled supply air min temp |  | 0.00 | 30.00 | C | 16.00 | 1.28
4x0833 | Seasonal controlled supply air max temp |  | 8.00 | 50.00 | C | 28.00 | 1.28
4x0834 | Extra regulation 2 combi coil output indication | 0=Heat, 1=Cool | 0 | 1 |  | 0 | 2.37
4x0835
4x0836
4x0837
4x0838
4x0839
4x0840
4x0841
4x0842
4x0843
4x0844
4x0845
4x0846
4x0847
4x0848
4x0849
H/C
4x0850 | H/C heat mode | 0=Standard, 1=Comfort | 0 | 1 |  | 0 | 1.23
4x0851 | H/C cool mode | 0=Standard, 1=Comfort | 0 | 1 |  | 0 | 1.23
4x0852 | H/C outdoor temperature limit heating |  | -50.00 | 50.00 | °C | -20.00 | 1.23
4x0853 | H/C outdoor temperature limit cooling |  | 0.00 | 50.00 | °C | 15.00 | 1.23
4x0854 | H/C air flow limit supply air |  | 0 | 3x00057 | l/s |  | 1.23
4x0855 | H/C air flow limit extract air |  | 0 | 3x00058 | l/s |  | 1.23
4x0856
4x0857
4x0858
4x0859
4x0860
4x0861
4x0862
4x0863
4x0864
4x0865
4x0866
4x0867
4x0868
4x0869
4x0870
4x0871
4x0872
4x0873
4x0874
4x0875
4x0876
4x0877
4x0878
4x0879
4x0880
4x0881
4x0882
4x0883
4x0884
4x0885
4x0886
4x0887
4x0888
4x0889
Humidifying
4x0890 | Humidifying time 1 (days) | 0=Inactive, 1=Monday, 2=Tuesday, 3=Wednesday, 4=Thursday, 5=Friday, 6=Saturday, 7=Sunday, 8=Monday to Friday, 9= Monday to Sunday, 10=Saturday to Sunday. | 0 | 10 |  | 0 | 2.37
4x0891 | Humidifying start time 1 (hour) |  | 0 | 23 | h | 0 | 2.37
4x0892 | Humidifying start time 1 (minute) |  | 0 | 59 | min | 0 | 2.37
4x0893 | Humidifying stop time 1 (hour) |  | 0 | 23 | h | 0 | 2.37
4x0894 | Humidifying stop time 1 (minute) |  | 0 | 59 | min | 0 | 2.37
4x0895 | Humidifying time 2 (days) | 0=Inactive, 1=Monday, 2=Tuesday, 3=Wednesday, 4=Thursday, 5=Friday, 6=Saturday, 7=Sunday, 8=Monday to Friday, 9= Monday to Sunday, 10=Saturday to Sunday. | 0 | 10 |  | 0 | 2.37
4x0896 | Humidifying start time 2 (hour) |  | 0 | 23 | h | 0 | 2.37
4x0897 | Humidifying start time 2 (minute) |  | 0 | 59 | min | 0 | 2.37
4x0898 | Humidifying stop time 2 (hour) |  | 0 | 23 | h | 0 | 2.37
4x0899 | Humidifying stop time 2 (minute) |  | 0 | 59 | min | 0 | 2.37
4x0900 | Humidifying time 3 (days) | 0=Inactive, 1=Monday, 2=Tuesday, 3=Wednesday, 4=Thursday, 5=Friday, 6=Saturday, 7=Sunday, 8=Monday to Friday, 9= Monday to Sunday, 10=Saturday to Sunday. | 0 | 10 |  | 0 | 2.37
4x0901 | Humidifying start time 3 (hour) |  | 0 | 23 | h | 0 | 2.37
4x0902 | Humidifying start time 3 (minute) |  | 0 | 59 | min | 0 | 2.37
4x0903 | Humidifying stop time 3 (hour) |  | 0 | 23 | h | 0 | 2.37
4x0904 | Humidifying stop time 3 (minute) |  | 0 | 59 | min | 0 | 2.37
4x0905 | Humidifying time 4 (days) | 0=Inactive, 1=Monday, 2=Tuesday, 3=Wednesday, 4=Thursday, 5=Friday, 6=Saturday, 7=Sunday, 8=Monday to Friday, 9= Monday to Sunday, 10=Saturday to Sunday. | 0 | 10 |  | 0 | 2.37
4x0906 | Humidifying start time 4 (hour) |  | 0 | 23 | h | 0 | 2.37
4x0907 | Humidifying start time 4 (minute) |  | 0 | 59 | min | 0 | 2.37
4x0908 | Humidifying stop time 4 (hour) |  | 0 | 23 | h | 0 | 2.37
4x0909 | Humidifying stop time 4 (minute) |  | 0 | 59 | min | 0 | 2.37
4x0910 | Humidifying start time | Humidifying time channel start level | 10.00 | 4x0911 | %RH | 50.00 | 2.37
4x0911 | Humidifying stop time | Humidifying time channel stop level | 4x0910 | 95.00 | %RH | 55.00 | 2.37
4x0912 | Humidifying time | Humidifying time channel set point | 10.00 | 95.00 | %RH | 40.00 | 2.37
4x0913
4x0914
4x0915
Time schedule
4x0916 | Year | Setting for the unit's internal clock | 2000 | 2099 |  | 2000
4x0917 | Month | Setting for the unit's internal clock | 1 | 12 |  | 1
4x0918 | Date | Setting for the unit's internal clock | 1 | 31 |  | 1
4x0919 | Hour | Setting for the unit's internal clock | 0 | 23 |  | 0
4x0920 | Minute | Setting for the unit's internal clock | 0 | 59 |  | 0
4x0921 | Second | Setting for the unit's internal clock | 0 | 59 |  | 0
4x0922
4x0923
4x0924
4x0925
4x0926
4x0927
4x0928
4x0929
4x0930
4x0931
4x0932 | Default action | 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop | 1 | 5 |  | 2
4x0933 | Effective period always | 0=Off, 1=On | 0 | 1 |  | 1
4x0934 | Effective period, Start year | 0=Unspecified | 2000 | 2099 |  | 2000
4x0935 | Effective period, Start month | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x0936 | Effective period, Start date | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
4x0937 | Effective period, Start week day | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x0938 | Effective period, Stop year | 0=Unspecified | 2000 | 2099 |  | 2000
4x0939 | Effective period, Stop month | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x0940 | Effective period, Stop date | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
4x0941 | Effective period, Stop week day | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x0942 | Day schedule, Monday hour #1 |  | 0 | 23 | h | 0
4x0943 | Day schedule, Monday hour #2 |  | 0 | 23 | h | 0
4x0944 | Day schedule, Monday hour #3 |  | 0 | 23 | h | 0
4x0945 | Day schedule, Monday hour #4 |  | 0 | 23 | h | 0
4x0946 | Day schedule, Monday hour #5 |  | 0 | 23 | h | 0
4x0947 | Day schedule, Monday hour #6 |  | 0 | 23 | h | 0
4x0948 | Day schedule, Monday minute #1 |  | 0 | 59 | min | 0
4x0949 | Day schedule, Monday minute #2 |  | 0 | 59 | min | 0
4x0950 | Day schedule, Monday minute #3 |  | 0 | 59 | min | 0
4x0951 | Day schedule, Monday minute #4 |  | 0 | 59 | min | 0
4x0952 | Day schedule, Monday minute #5 |  | 0 | 59 | min | 0
4x0953 | Day schedule, Monday minute #6 |  | 0 | 59 | min | 0
4x0954 | Day schedule, Monday action #1 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x0955 | Day schedule, Monday action #2 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x0956 | Day schedule, Monday action #3 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x0957 | Day schedule, Monday action #4 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x0958 | Day schedule, Monday action #5 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x0959 | Day schedule, Monday action #6 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x0960 | Day schedule, Tuesday hour #1 |  | 0 | 23 | h | 0
4x0961 | Day schedule, Tuesday hour #2 |  | 0 | 23 | h | 0
4x0962 | Day schedule, Tuesday hour #3 |  | 0 | 23 | h | 0
4x0963 | Day schedule, Tuesday hour #4 |  | 0 | 23 | h | 0
4x0964 | Day schedule, Tuesday hour #5 |  | 0 | 23 | h | 0
4x0965 | Day schedule, Tuesday hour #6 |  | 0 | 23 | h | 0
4x0966 | Day schedule, Tuesday minute #1 |  | 0 | 59 | min | 0
4x0967 | Day schedule, Tuesday minute #2 |  | 0 | 59 | min | 0
4x0968 | Day schedule, Tuesday minute #3 |  | 0 | 59 | min | 0
4x0969 | Day schedule, Tuesday minute #4 |  | 0 | 59 | min | 0
4x0970 | Day schedule, Tuesday minute #5 |  | 0 | 59 | min | 0
4x0971 | Day schedule, Tuesday minute #6 |  | 0 | 59 | min | 0
4x0972 | Day schedule, Tuesday action #1 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x0973 | Day schedule, Tuesday action #2 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x0974 | Day schedule, Tuesday action #3 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x0975 | Day schedule, Tuesday action #4 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x0976 | Day schedule, Tuesday action #5 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x0977 | Day schedule, Tuesday action #6 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x0978 | Day schedule, Wednesday hour #1 |  | 0 | 23 | h | 0
4x0979 | Day schedule, Wednesday hour #2 |  | 0 | 23 | h | 0
4x0980 | Day schedule, Wednesday hour #3 |  | 0 | 23 | h | 0
4x0981 | Day schedule, Wednesday hour #4 |  | 0 | 23 | h | 0
4x0982 | Day schedule, Wednesday hour #5 |  | 0 | 23 | h | 0
4x0983 | Day schedule, Wednesday hour #6 |  | 0 | 23 | h | 0
4x0984 | Day schedule, Wednesday minute #1 |  | 0 | 59 | min | 0
4x0985 | Day schedule, Wednesday minute #2 |  | 0 | 59 | min | 0
4x0986 | Day schedule, Wednesday minute #3 |  | 0 | 59 | min | 0
4x0987 | Day schedule, Wednesday minute #4 |  | 0 | 59 | min | 0
4x0988 | Day schedule, Wednesday minute #5 |  | 0 | 59 | min | 0
4x0989 | Day schedule, Wednesday minute #6 |  | 0 | 59 | min | 0
4x0990 | Day schedule, Wednesday action #1 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x0991 | Day schedule, Wednesday action #2 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x0992 | Day schedule, Wednesday action #3 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x0993 | Day schedule, Wednesday action #4 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x0994 | Day schedule, Wednesday action #5 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x0995 | Day schedule, Wednesday action #6 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x0996 | Day schedule, Thursday hour #1 |  | 0 | 23 | h | 0
4x0997 | Day schedule, Thursday hour #2 |  | 0 | 23 | h | 0
4x0998 | Day schedule, Thursday hour #3 |  | 0 | 23 | h | 0
4x0999 | Day schedule, Thursday hour #4 |  | 0 | 23 | h | 0
4x1000 | Day schedule, Thursday hour #5 |  | 0 | 23 | h | 0
4x1001 | Day schedule, Thursday hour #6 |  | 0 | 23 | h | 0
4x1002 | Day schedule, Thursday minute #1 |  | 0 | 59 | min | 0
4x1003 | Day schedule, Thursday minute #2 |  | 0 | 59 | min | 0
4x1004 | Day schedule, Thursday minute #3 |  | 0 | 59 | min | 0
4x1005 | Day schedule, Thursday minute #4 |  | 0 | 59 | min | 0
4x1006 | Day schedule, Thursday minute #5 |  | 0 | 59 | min | 0
4x1007 | Day schedule, Thursday minute #6 |  | 0 | 59 | min | 0
4x1008 | Day schedule, Thursday action #1 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x1009 | Day schedule, Thursday action #2 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x1010 | Day schedule, Thursday action #3 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x1011 | Day schedule, Thursday action #4 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x1012 | Day schedule, Thursday action #5 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x1013 | Day schedule, Thursday action #6 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x1014 | Day schedule, Friday hour #1 |  | 0 | 23 | h | 0
4x1015 | Day schedule, Friday hour #2 |  | 0 | 23 | h | 0
4x1016 | Day schedule, Friday hour #3 |  | 0 | 23 | h | 0
4x1017 | Day schedule, Friday hour #4 |  | 0 | 23 | h | 0
4x1018 | Day schedule, Friday hour #5 |  | 0 | 23 | h | 0
4x1019 | Day schedule, Friday hour #6 |  | 0 | 23 | h | 0
4x1020 | Day schedule, Friday minute #1 |  | 0 | 59 | min | 0
4x1021 | Day schedule, Friday minute #2 |  | 0 | 59 | min | 0
4x1022 | Day schedule, Friday minute #3 |  | 0 | 59 | min | 0
4x1023 | Day schedule, Friday minute #4 |  | 0 | 59 | min | 0
4x1024 | Day schedule, Friday minute #5 |  | 0 | 59 | min | 0
4x1025 | Day schedule, Friday minute #6 |  | 0 | 59 | min | 0
4x1026 | Day schedule, Friday action #1 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x1027 | Day schedule, Friday action #2 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x1028 | Day schedule, Friday action #3 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x1029 | Day schedule, Friday action #4 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x1030 | Day schedule, Friday action #5 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x1031 | Day schedule, Friday action #6 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x1032 | Day schedule, Saturday hour #1 |  | 0 | 23 | h | 0
4x1033 | Day schedule, Saturday hour #2 |  | 0 | 23 | h | 0
4x1034 | Day schedule, Saturday hour #3 |  | 0 | 23 | h | 0
4x1035 | Day schedule, Saturday hour #4 |  | 0 | 23 | h | 0
4x1036 | Day schedule, Saturday hour #5 |  | 0 | 23 | h | 0
4x1037 | Day schedule, Saturday hour #6 |  | 0 | 23 | h | 0
4x1038 | Day schedule, Saturday minute #1 |  | 0 | 59 | min | 0
4x1039 | Day schedule, Saturday minute #2 |  | 0 | 59 | min | 0
4x1040 | Day schedule, Saturday minute #3 |  | 0 | 59 | min | 0
4x1041 | Day schedule, Saturday minute #4 |  | 0 | 59 | min | 0
4x1042 | Day schedule, Saturday minute #5 |  | 0 | 59 | min | 0
4x1043 | Day schedule, Saturday minute #6 |  | 0 | 59 | min | 0
4x1044 | Day schedule, Saturday action #1 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x1045 | Day schedule, Saturday action #2 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x1046 | Day schedule, Saturday action #3 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x1047 | Day schedule, Saturday action #4 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x1048 | Day schedule, Saturday action #5 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x1049 | Day schedule, Saturday action #6 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x1050 | Day schedule, Sunday hour #1 |  | 0 | 23 | h | 0
4x1051 | Day schedule, Sunday hour #2 |  | 0 | 23 | h | 0
4x1052 | Day schedule, Sunday hour #3 |  | 0 | 23 | h | 0
4x1053 | Day schedule, Sunday hour #4 |  | 0 | 23 | h | 0
4x1054 | Day schedule, Sunday hour #5 |  | 0 | 23 | h | 0
4x1055 | Day schedule, Sunday hour #6 |  | 0 | 23 | h | 0
4x1056 | Day schedule, Sunday minute #1 |  | 0 | 59 | min | 0
4x1057 | Day schedule, Sunday minute #2 |  | 0 | 59 | min | 0
4x1058 | Day schedule, Sunday minute #3 |  | 0 | 59 | min | 0
4x1059 | Day schedule, Sunday minute #4 |  | 0 | 59 | min | 0
4x1060 | Day schedule, Sunday minute #5 |  | 0 | 59 | min | 0
4x1061 | Day schedule, Sunday minute #6 |  | 0 | 59 | min | 0
4x1062 | Day schedule, Sunday action #1 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x1063 | Day schedule, Sunday action #2 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x1064 | Day schedule, Sunday action #3 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x1065 | Day schedule, Sunday action #4 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x1066 | Day schedule, Sunday action #5 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x1067 | Day schedule, Sunday action #6 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 0 | 1.11
4x1068 | Exception schedule 1, function | 0=Date setting valid (MaxStartDate = 34) 1=Date range setting valid (MaxStartDate = 34) 2=Weekday setting valid (MaxStartDate = 6) 3=Calendar-1 setting valid 4=Calendar-2 setting valid 5=Inactive | 0 | 5 |  | 3 | 1.11
4x1069 | Exception schedule 1, start year | 0=Unspecified | 2000 | 2099 |  | 2000
4x1070 | Exception schedule 1, start month | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1071 | Exception schedule 1, start date | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
4x1072 | Exception schedule 1, start week day | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1073 | Exception schedule 1, stop year | 0=Unspecified | 2000 | 2099 |  | 2000
4x1074 | Exception schedule 1, stop month | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1075 | Exception schedule 1, stop date | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
4x1076 | Exception schedule 1, stop week day | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1077 | Exception schedule 1, priority | Lowest value = highest priority (if both exception 1 and 2 are active, and both "EventPriority" is equal, exception-1 has highest priority) | 1 | 16 |  | 0
4x1078 | Exception schedule 2, function | 0=Date setting valid (MaxStartDate = 34) 1=Date range setting valid (MaxStartDate = 34) 2=Weekday setting valid (MaxStartDate = 6) 3=Calendar-1 setting valid 4=Calendar-2 setting valid 5=Inactive | 0 | 5 |  | 4 | 1.16
4x1079 | Exception schedule 2, start year | 0=Unspecified | 2000 | 2099 |  | 2000
4x1080 | Exception schedule 2, start month | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1081 | Exception schedule 2, start date | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
4x1082 | Exception schedule 2, start week day | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1083 | Exception schedule 2, stop year | 0=Unspecified | 2000 | 2099 |  | 2000
4x1084 | Exception schedule 2, stop month | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1085 | Exception schedule 2, stop date | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
4x1086 | Exception schedule 2, stop week day | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1087 | Exception schedule 2, priority | Lowest value = highest priority (if both exception 1 and 2 are active, and both "EventPriority" is equal, exception-1 has highest priority) | 1 | 16 |  | 0
4x1088 | Calendar 1, function #1 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
4x1089 | Calendar 1, function #2 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
4x1090 | Calendar 1, function #3 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
4x1091 | Calendar 1, function #4 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
4x1092 | Calendar 1, function #5 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
4x1093 | Calendar 1, function #6 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
4x1094 | Calendar 1, function #7 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
4x1095 | Calendar 1, function #8 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
4x1096 | Calendar 1, function #9 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
4x1097 | Calendar 1, function #10 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
4x1098 | Calendar 1, Start year #1 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1099 | Calendar 1, Start year #2 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1100 | Calendar 1, Start year #3 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1101 | Calendar 1, Start year #4 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1102 | Calendar 1, Start year #5 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1103 | Calendar 1, Start year #6 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1104 | Calendar 1, Start year #7 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1105 | Calendar 1, Start year #8 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1106 | Calendar 1, Start year #9 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1107 | Calendar 1, Start year #10 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1108 | Calendar 1, Start month #1 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1109 | Calendar 1, Start month #2 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1110 | Calendar 1, Start month #3 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1111 | Calendar 1, Start month #4 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1112 | Calendar 1, Start month #5 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1113 | Calendar 1, Start month #6 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1114 | Calendar 1, Start month #7 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1115 | Calendar 1, Start month #8 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1116 | Calendar 1, Start month #9 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1117 | Calendar 1, Start month #10 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1118 | Calendar 1, Start date #1 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
4x1119 | Calendar 1, Start date #2 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
4x1120 | Calendar 1, Start date #3 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
4x1121 | Calendar 1, Start date #4 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
4x1122 | Calendar 1, Start date #5 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
4x1123 | Calendar 1, Start date #6 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
4x1124 | Calendar 1, Start date #7 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
4x1125 | Calendar 1, Start date #8 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
4x1126 | Calendar 1, Start date #9 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
4x1127 | Calendar 1, Start date #10 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
4x1128 | Calendar 1, Start week day #1 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1129 | Calendar 1, Start week day #2 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1130 | Calendar 1, Start week day #3 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1131 | Calendar 1, Start week day #4 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1132 | Calendar 1, Start week day #5 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1133 | Calendar 1, Start week day #6 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1134 | Calendar 1, Start week day #7 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1135 | Calendar 1, Start week day #8 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1136 | Calendar 1, Start week day #9 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1137 | Calendar 1, Start week day #10 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1138 | Calendar 1, Stop year #1 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1139 | Calendar 1, Stop year #2 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1140 | Calendar 1, Stop year #3 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1141 | Calendar 1, Stop year #4 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1142 | Calendar 1, Stop year #5 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1143 | Calendar 1, Stop year #6 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1144 | Calendar 1, Stop year #7 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1145 | Calendar 1, Stop year #8 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1146 | Calendar 1, Stop year #9 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1147 | Calendar 1, Stop year #10 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1148 | Calendar 1, Stop month #1 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1149 | Calendar 1, Stop month #2 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1150 | Calendar 1, Stop month #3 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1151 | Calendar 1, Stop month #4 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1152 | Calendar 1, Stop month #5 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1153 | Calendar 1, Stop month #6 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1154 | Calendar 1, Stop month #7 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1155 | Calendar 1, Stop month #8 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1156 | Calendar 1, Stop month #9 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1157 | Calendar 1, Stop month #10 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1158 | Calendar 1, Stop date #1 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
4x1159 | Calendar 1, Stop date #2 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
4x1160 | Calendar 1, Stop date #3 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
4x1161 | Calendar 1, Stop date #4 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
4x1162 | Calendar 1, Stop date #5 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
4x1163 | Calendar 1, Stop date #6 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
4x1164 | Calendar 1, Stop date #7 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
4x1165 | Calendar 1, Stop date #8 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
4x1166 | Calendar 1, Stop date #9 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
4x1167 | Calendar 1, Stop date #10 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
4x1168 | Calendar 1, Stop week day #1 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1169 | Calendar 1, Stop week day #2 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1170 | Calendar 1, Stop week day #3 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1171 | Calendar 1, Stop week day #4 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1172 | Calendar 1, Stop week day #5 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1173 | Calendar 1, Stop week day #6 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1174 | Calendar 1, Stop week day #7 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1175 | Calendar 1, Stop week day #8 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1176 | Calendar 1, Stop week day #9 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1177 | Calendar 1, Stop week day #10 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1178 | Calendar 2, function #1 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
4x1179 | Calendar 2, function #2 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
4x1180 | Calendar 2, function #3 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
4x1181 | Calendar 2, function #4 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
4x1182 | Calendar 2, function #5 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
4x1183 | Calendar 2, function #6 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
4x1184 | Calendar 2, function #7 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
4x1185 | Calendar 2, function #8 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
4x1186 | Calendar 2, function #9 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
4x1187 | Calendar 2, function #10 | 0=Date (MaxStartDate = 34) 1=Date range (MaxStartDate = 34) 2=Weekday (MaxStartDate = 6) 3=Inactive | 0 | 3 |  | 3 | 1.11
4x1188 | Calendar 2, Start year #1 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1189 | Calendar 2, Start year #2 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1190 | Calendar 2, Start year #3 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1191 | Calendar 2, Start year #4 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1192 | Calendar 2, Start year #5 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1193 | Calendar 2, Start year #6 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1194 | Calendar 2, Start year #7 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1195 | Calendar 2, Start year #8 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1196 | Calendar 2, Start year #9 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1197 | Calendar 2, Start year #10 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1198 | Calendar 2, Start month #1 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1199 | Calendar 2, Start month #2 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1200 | Calendar 2, Start month #3 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1201 | Calendar 2, Start month #4 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1202 | Calendar 2, Start month #5 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1203 | Calendar 2, Start month #6 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1204 | Calendar 2, Start month #7 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1205 | Calendar 2, Start month #8 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1206 | Calendar 2, Start month #9 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1207 | Calendar 2, Start month #10 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1208 | Calendar 2, Start date #1 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
4x1209 | Calendar 2, Start date #2 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
4x1210 | Calendar 2, Start date #3 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
4x1211 | Calendar 2, Start date #4 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
4x1212 | Calendar 2, Start date #5 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
4x1213 | Calendar 2, Start date #6 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
4x1214 | Calendar 2, Start date #7 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
4x1215 | Calendar 2, Start date #8 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
4x1216 | Calendar 2, Start date #9 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
4x1217 | Calendar 2, Start date #10 | 0=Unspecified -------------------Max = 34-------------- 32=Last day of month 33=odd days of month 34=even days of month -------------------Max = 6---------------- 1=days numbered 1..7 2=days numbered 8..14 3=days numbered 15..21 4=days numbered 22.28 5=days numbered 29..31 6=last 7 days of month | 0 | 34 |  | 0
4x1218 | Calendar 2, Start week day #1 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1219 | Calendar 2, Start week day #2 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1220 | Calendar 2, Start week day #3 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1221 | Calendar 2, Start week day #4 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1222 | Calendar 2, Start week day #5 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1223 | Calendar 2, Start week day #6 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1224 | Calendar 2, Start week day #7 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1225 | Calendar 2, Start week day #8 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1226 | Calendar 2, Start week day #9 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1227 | Calendar 2, Start week day #10 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1228 | Calendar 2, Stop year #1 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1229 | Calendar 2, Stop year #2 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1230 | Calendar 2, Stop year #3 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1231 | Calendar 2, Stop year #4 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1232 | Calendar 2, Stop year #5 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1233 | Calendar 2, Stop year #6 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1234 | Calendar 2, Stop year #7 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1235 | Calendar 2, Stop year #8 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1236 | Calendar 2, Stop year #9 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1237 | Calendar 2, Stop year #10 | 0=Unspecified | 2000 | 2099 |  | 2000
4x1238 | Calendar 2, Stop month #1 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1239 | Calendar 2, Stop month #2 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1240 | Calendar 2, Stop month #3 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1241 | Calendar 2, Stop month #4 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1242 | Calendar 2, Stop month #5 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1243 | Calendar 2, Stop month #6 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1244 | Calendar 2, Stop month #7 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1245 | Calendar 2, Stop month #8 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1246 | Calendar 2, Stop month #9 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1247 | Calendar 2, Stop month #10 | 0=Unspecified, 1-12=Jan..Dec, 13=Odd months, 14=Even months | 0 | 14 |  | 0
4x1248 | Calendar 2, Stop date #1 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
4x1249 | Calendar 2, Stop date #2 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
4x1250 | Calendar 2, Stop date #3 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
4x1251 | Calendar 2, Stop date #4 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
4x1252 | Calendar 2, Stop date #5 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
4x1253 | Calendar 2, Stop date #6 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
4x1254 | Calendar 2, Stop date #7 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
4x1255 | Calendar 2, Stop date #8 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
4x1256 | Calendar 2, Stop date #9 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
4x1257 | Calendar 2, Stop date #10 | 0=Unspecified, 1-31=Jan..Dec, 32=Last day, 33=Odd days, 34=Even days | 0 | 34 |  | 0
4x1258 | Calendar 2, Stop week day #1 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1259 | Calendar 2, Stop week day #2 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1260 | Calendar 2, Stop week day #3 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1261 | Calendar 2, Stop week day #4 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1262 | Calendar 2, Stop week day #5 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1263 | Calendar 2, Stop week day #6 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1264 | Calendar 2, Stop week day #7 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1265 | Calendar 2, Stop week day #8 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1266 | Calendar 2, Stop week day #9 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1267 | Calendar 2, Stop week day #10 | 0=Unspecified, 1-7=Mon..Sun | 0 | 7 |  | 0
4x1268 | Prolonged low speed hours | Setting for prolonged external low speed operation. | 0 | 23 |  | 0 | 1.13
4x1269 | Prolonged low speed minutes | Setting for prolonged external low speed operation. | 0 | 59 |  | 0 | 1.13
4x1270 | Prolonged high speed hours | Setting for prolonged external high speed operation. | 0 | 23 |  | 0 | 1.13
4x1271 | Prolonged high speed minutes | Setting for prolonged external high speed operation. | 0 | 59 |  | 0 | 1.13
4x1272 | Exception schedule 1, Hour #1 |  | 0 | 23 | h | 0 | 1.13
4x1273 | Exception schedule 1, Hour #2 |  | 0 | 23 | h | 0 | 1.13
4x1274 | Exception schedule 1, Hour #3 |  | 0 | 23 | h | 0 | 1.13
4x1275 | Exception schedule 1, Hour #4 |  | 0 | 23 | h | 0 | 1.13
4x1276 | Exception schedule 1, Hour #5 |  | 0 | 23 | h | 0 | 1.13
4x1277 | Exception schedule 1, Hour #6 |  | 0 | 23 | h | 0 | 1.13
4x1278 | Exception schedule 1, Minute #1 |  | 0 | 59 | min | 0 | 1.13
4x1279 | Exception schedule 1, Minute #2 |  | 0 | 59 | min | 0 | 1.13
4x1280 | Exception schedule 1, Minute #3 |  | 0 | 59 | min | 0 | 1.13
4x1281 | Exception schedule 1, Minute #4 |  | 0 | 59 | min | 0 | 1.13
4x1282 | Exception schedule 1, Minute #5 |  | 0 | 59 | min | 0 | 1.13
4x1283 | Exception schedule 1, Minute #6 |  | 0 | 59 | min | 0 | 1.13
4x1284 | Exception schedule 1, Action #1 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 1 | 1.13
4x1285 | Exception schedule 1, Action #2 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 1 | 1.13
4x1286 | Exception schedule 1, Action #3 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 1 | 1.13
4x1287 | Exception schedule 1, Action #4 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 1 | 1.13
4x1288 | Exception schedule 1, Action #5 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 1 | 1.13
4x1289 | Exception schedule 1, Action #6 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 1 | 1.13
4x1290 | Exception schedule 2, Hour #1 |  | 0 | 23 | h | 0 | 1.13
4x1291 | Exception schedule 2, Hour #2 |  | 0 | 23 | h | 0 | 1.13
4x1292 | Exception schedule 2, Hour #3 |  | 0 | 23 | h | 0 | 1.13
4x1293 | Exception schedule 2, Hour #4 |  | 0 | 23 | h | 0 | 1.13
4x1294 | Exception schedule 2, Hour #5 |  | 0 | 23 | h | 0 | 1.13
4x1295 | Exception schedule 2, Hour #6 |  | 0 | 23 | h | 0 | 1.13
4x1296 | Exception schedule 2, Minute #1 |  | 0 | 59 | min | 0 | 1.13
4x1297 | Exception schedule 2, Minute #2 |  | 0 | 59 | min | 0 | 1.13
4x1298 | Exception schedule 2, Minute #3 |  | 0 | 59 | min | 0 | 1.13
4x1299 | Exception schedule 2, Minute #4 |  | 0 | 59 | min | 0 | 1.13
4x1300 | Exception schedule 2, Minute #5 |  | 0 | 59 | min | 0 | 1.13
4x1301 | Exception schedule 2, Minute #6 |  | 0 | 59 | min | 0 | 1.13
4x1302 | Exception schedule 2, Action #1 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 4 | 1.13
4x1303 | Exception schedule 2, Action #2 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 4 | 1.13
4x1304 | Exception schedule 2, Action #3 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 4 | 1.13
4x1305 | Exception schedule 2, Action #4 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 4 | 1.13
4x1306 | Exception schedule 2, Action #5 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 4 | 1.13
4x1307 | Exception schedule 2, Action #6 | 0=Inactive, 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop, 6=Ignore. | 0 | 6 |  | 4 | 1.13